Legionella Risk Assessment for Temporary Systems

Health & Safety – Water Safety

This assessment is carried out in accordance with the HSE Approved Code of Practice L8 ‘Legionnaires’ disease: The control of legionella bacteria in water systems’ and HSE guidance HSG274 Parts 1–3. It covers all temporary water systems on the construction site including welfare facilities, drinking water, showers, hot water systems, hoses and water bowsers. Legionella bacteria thrive between 20–45°C and are a risk wherever water is stored or distributed and can create an aerosol or be inhaled.

| Document Ref: | Enter document reference |
| --- | --- |
| Revision: | Enter revision number |
| Date: | DD / MM / YYYY |
| Project Name: | Enter project name |
| Contract No: | Enter contract number |
| Assessed By: | Enter name, role and competence (e.g. City & Guilds legionella, BOHS P901) |
| Approved By: | Enter name and role |

# Responsible Persons

| Duty Holder: | Enter name and role of person with overall responsibility for legionella control |
| --- | --- |
| Responsible Person: | Enter name and role of person managing day-to-day water safety on site |
| Water Treatment Company: | Enter company name and contract reference (if applicable) |
| Competent Assessor: | Enter name and qualifications of person carrying out this risk assessment |

# Site Water System Inventory

| Mains Water Supply: | Enter source (mains connection point, temporary supply, borehole) |
| --- | --- |
| Incoming Mains Temp: | Enter temperature at the incoming supply (°C) |
| Cold Water Storage: | Describe cold water storage arrangements (tank type, size, location, insulation) |
| Hot Water Generation: | Describe hot water system (calorifier, point-of-use, instantaneous) |
| Hot Water Storage Temp: | Enter calorifier/storage temperature (°C) |
| Welfare Units Served: | List welfare units connected (canteen, toilets, showers, drying room) |
| Number of Showers: | Enter number |
| Number of Outlets (taps): | Enter total number of hot and cold outlets |
| Water Bowsers on Site: | Enter number and capacity |
| Hose Pipes in Use: | Enter number and locations |

# Water System Risk Assessment

Assess each water system component for legionella risk. Identify the hazard, existing controls and any additional actions required.

| No. | System Component | Risk / Hazard | Control Measures | Risk Level | Action Needed |
| --- | --- | --- | --- | --- | --- |
| 1 | Cold water storage tanks (header tanks) | Stagnation, warm temperature in summer, debris ingress, inadequate turnover | Ensure tanks are covered, insulated, fitted with screened overflow. Maintain cold water below 20°C. Size tank to ensure regular turnover (ideally daily). Inspect and clean annually. |  |  |
| 2 | Hot water systems (calorifiers, point-of-use heaters) | Temperature below 60°C at the calorifier or below 50°C at outlets | Store hot water at 60°C minimum. Distribute at 50°C minimum (55°C recommended). Confirm thermostat settings. Monthly temperature checks. |  |  |
| 3 | Dead legs and little-used outlets | Stagnation in pipework that is rarely used, allowing bacterial growth | Identify and remove dead legs where possible. Flush little-used outlets weekly for 2 minutes. Consider removing unused outlets. |  |  |
| 4 | Showers in welfare facilities | Aerosol generation creating inhalable water droplets; warm water temperatures | Flush showers weekly if not used daily. Descale and disinfect shower heads quarterly. Maintain water temperature above 50°C at the outlet or below 20°C for cold. Replace flexible hoses annually. |  |  |
| 5 | Hose pipes and temporary water supplies | Water standing in hoses in warm weather, creating ideal growth conditions | Drain hoses after each use. Do not leave hoses in direct sunlight. Replace hoses that are damaged or discoloured. Use drinking-water-approved hose materials for potable supplies. |  |  |
| 6 | Water bowsers and mobile tanks | Stagnation, contamination, warm temperatures in summer | Empty and clean water bowsers regularly (minimum weekly in warm weather). Do not allow water to stand for more than 24 hours. Ensure bowsers are covered. Use potable-grade bowsers for drinking water. |  |  |
| 7 | Cooling systems / evaporative condensers | High risk – aerosol generation, warm water, nutrients from biological growth | If present, must be registered with the local authority. Full L8 risk assessment required. Specialist water treatment programme. Monthly monitoring by competent water treatment company. |  |  |
| 8 | Emergency showers and eyewash stations | Stagnation if not flushed regularly | Flush weekly and record. Check temperature is safe. Inspect for contamination. Service annually. |  |  |
| 9 | Fire sprinkler systems (wet pipe) | Stagnation in standing water; low risk unless disturbed | Generally low risk if undisturbed. Include in legionella risk assessment. No action unless system is drained and refilled (flush and disinfect before recommissioning). |  |  |
| 10 | Mains-fed drinking water dispensers | Low risk if properly maintained; biofilm in internal components | Service in accordance with manufacturer’s instructions. Replace filters as recommended. Clean and sanitise regularly. |  |  |

# Temperature Control Guide

| Temperature Range | Legionella Risk | Action |
| --- | --- | --- |
| Below 20°C | Low – Bacteria dormant | Maintain cold water below 20°C |
| 20–45°C | HIGH – Ideal growth range | Danger zone. Minimise time water spends in this range. Investigate and correct. |
| Above 50°C | Bacteria killed slowly | Distribute hot water at 50°C minimum at the outlet |
| Above 60°C | Bacteria killed rapidly | Store hot water at 60°C minimum in the calorifier |

# Legionella Control Checklist

| No. | Control Measure | Yes | No | N/A | Initials |
| --- | --- | --- | --- | --- | --- |
| 1 | A competent person (as defined in L8) has been appointed to manage legionella risk on site |  |  |  |  |
| 2 | Responsible person is named in the site water safety log book |  |  |  |  |
| 3 | Written scheme of control (this assessment and the monitoring schedule) is in place |  |  |  |  |
| 4 | All temporary water systems on site have been identified and included in this assessment |  |  |  |  |
| 5 | Cold water storage tanks are covered, insulated and protected from heat sources and sunlight |  |  |  |  |
| 6 | Cold water is maintained below 20°C (check monthly at representative outlets) |  |  |  |  |
| 7 | Hot water is stored at 60°C minimum and distributed at 50°C minimum |  |  |  |  |
| 8 | Hot water reaches 50°C at the outlet within one minute of running |  |  |  |  |
| 9 | All dead legs have been identified and either removed or flushed weekly |  |  |  |  |
| 10 | Little-used outlets (used less than once per week) are flushed for 2 minutes weekly and recorded |  |  |  |  |
| 11 | Showers are descaled and disinfected quarterly |  |  |  |  |
| 12 | Flexible shower hoses are replaced annually |  |  |  |  |
| 13 | Water bowsers and mobile tanks are emptied and cleaned weekly (or more frequently in warm weather) |  |  |  |  |
| 14 | Hose pipes are drained after use and not left with standing water |  |  |  |  |
| 15 | Temperature monitoring is carried out monthly at sentinel outlets and recorded |  |  |  |  |
| 16 | Water sampling for legionella is carried out as required by the risk assessment (typically quarterly or after a system change) |  |  |  |  |
| 17 | Results of water sampling are reviewed by a competent person and action taken on any positive results |  |  |  |  |
| 18 | Annual inspection and cleaning of cold water storage tanks is scheduled |  |  |  |  |
| 19 | Records are maintained in the site water safety log book for a minimum of 5 years |  |  |  |  |
| 20 | All welfare facilities connected to temporary water systems have been included |  |  |  |  |
| 21 | Workers have been informed not to drink from non-potable water supplies |  |  |  |  |
| 22 | Non-potable water outlets are clearly labelled ‘NOT DRINKING WATER’ |  |  |  |  |

# Temperature Monitoring Schedule

Record monthly temperature checks at sentinel outlets (nearest and furthest from the storage tank / calorifier).

| Date | Outlet Location | Hot/Cold | Temp °C | Time to Temp | Compliant? | Checked By |
| --- | --- | --- | --- | --- | --- | --- |

# Little-Used Outlet Flushing Log

| Date | Outlet Location | Hot/Cold | Duration | Flushed By | Notes |
| --- | --- | --- | --- | --- | --- |

# Overall Legionella Risk Rating

□ LOW RISK – Controls adequate. Maintain monitoring schedule. □ MEDIUM RISK – Some improvements required. Address actions within agreed timescales. □ HIGH RISK – Significant deficiencies. Immediate action required. Consider isolating affected systems.

# Assessor Sign-Off

I confirm that this legionella risk assessment has been carried out by a competent person in accordance with L8 and HSG274. The findings and recommendations are recorded accurately.

| Assessor Name: |  | Date: |  |
| --- | --- | --- | --- |
| Signature: |  | Qualifications: |  |

# Duty Holder Acknowledgement

| Name: |  | Date: |  |
| --- | --- | --- | --- |
| Signature: |  | Review Date: |  |

# Notes / Additional Comments

Enter any additional notes or comments here.

# Document Control

| Revision | Date | Description of Change | Author | Approved By |
| --- | --- | --- | --- | --- |