Energisation Checklist

Safety-critical checklist to be completed prior to the initial energisation of any electrical system, switchboard, MCC, distribution board, or transformer. All items must be verified before permission to energise is granted. Completed in accordance with BS 7671 (IET Wiring Regulations), the Electricity at Work Regulations 1989, and the project electrical safety rules.

Project Details

| Document Ref: | Enter document reference |
| --- | --- |
| Revision: | Enter revision number |
| Energisation Permit No.: | Enter unique permit / certificate number |
| Date: | DD / MM / YYYY |
| Project Name: | Enter project name |
| Contract Number: | Enter contract number |
| Prepared By: | Name / role |
| Approved By: | Name / role (Authorised Person) |

System / Equipment Details

| System / Equipment Name: | Enter system or equipment designation |
| --- | --- |
| System Number: | Enter system identification number |
| Switchboard / MCC Reference: | Enter switchboard, MCC, or distribution board designation |
| Supply Voltage: | e.g. 11kV, 3.3kV, 415V, 230V |
| Supply Source: | Enter source transformer, generator, or incoming supply reference |
| Circuit Reference: | Enter circuit number or breaker reference |
| Cable Reference(s): | Enter cable schedule reference(s) |
| Location / Area: | Enter plant area, building, or substation reference |
| System Turnover Certificate Ref: | Enter RFSU / mechanical completion certificate reference |

Pre-Energisation Checks

ALL items must be confirmed as Yes or NA before energisation can proceed. Any item marked No must be resolved and re-checked.

| No. | Inspection / Check Item | Y / N / NA | Comments / Reference |
| --- | --- | --- | --- |
| 1 | System turnover certificate signed and all Category A punch items closed |  |  |
| 2 | Energisation method statement and risk assessment approved |  |  |
| 3 | All electrical installation inspection and test certificates complete (BS 7671) |  |  |
| 4 | Insulation resistance (Megger) tests complete and results acceptable |  |  |
| 5 | Continuity tests complete on all protective conductors |  |  |
| 6 | Earth electrode resistance tests complete and within design limits |  |  |
| 7 | Earth bonding verified to all exposed conductive parts and extraneous conductive parts |  |  |
| 8 | RCD trip tests complete (where RCDs are installed) |  |  |
| 9 | Cable terminations checked and torqued to manufacturer specification |  |  |
| 10 | All covers, shrouds, and barriers fitted to live parts |  |  |
| 11 | All cable entries sealed and IP rating of enclosures maintained |  |  |
| 12 | CT and VT connections verified correct ratio and polarity |  |  |
| 13 | Protection relay settings verified against protection coordination study |  |  |
| 14 | Interlocks tested and proven (mechanical, electrical, and key interlocks) |  |  |
| 15 | Emergency stop circuits tested and proven |  |  |
| 16 | Fire detection and suppression systems operational in electrical room / substation |  |  |
| 17 | Ventilation and cooling systems operational (transformer rooms, switchrooms, MCC rooms) |  |  |
| 18 | All temporary earths removed |  |  |
| 19 | All test leads, shorting links, and temporary connections removed |  |  |
| 20 | All equipment rated for the supply voltage and fault level |  |  |
| 21 | DSEAR / ATEX zoning requirements satisfied where applicable |  |  |
| 22 | Safety signage installed (danger of death, voltage labels, isolation point labels) |  |  |
| 23 | Exclusion zone established and barriers in place |  |  |
| 24 | All personnel briefed on energisation procedure and emergency arrangements |  |  |
| 25 | First aid and emergency arrangements in place (including burns kit) |  |  |
| 26 | DNO / IDNO notification made and approval received (if applicable) |  |  |

Permission to Energise

| All Pre-Energisation Checks Complete: | Yes / No |
| --- | --- |
| Permission to Energise Granted: | Yes / No |
| Energisation Date and Time: | DD / MM / YYYY at HH:MM |
| Authorised Person (AP) Name: | Enter name of Authorised Person granting permission |
| Switching Programme Reference: | Enter switching schedule / programme reference |

Post-Energisation Verification

| Voltages Confirmed Correct: | Record L1-L2, L2-L3, L3-L1, L-N, L-E readings |
| --- | --- |
| Phase Rotation Confirmed: | Enter phase rotation (R-Y-B / L1-L2-L3) |
| No Abnormal Noise or Smell: | Yes / No — describe if applicable |
| No Abnormal Heat Detected: | Yes / No — thermal check completed |
| Protection Devices Stable: | Yes / No — no spurious trips |
| Exclusion Zone Removed: | Yes / No — confirm safe access restored |

Sign-Off

| Role | Name | Signature | Date |
| --- | --- | --- | --- |
| Authorised Person (AP) |  |  | DD / MM / YYYY |
| Electrical Supervisor / Engineer |  |  | DD / MM / YYYY |
| Commissioning Engineer |  |  | DD / MM / YYYY |
| QA / QC Inspector |  |  | DD / MM / YYYY |
| Client / Employer Representative |  |  | DD / MM / YYYY |
| Health and Safety Adviser |  |  | DD / MM / YYYY |

Notes / Additional Comments

Enter any additional notes, test certificate references, DNO approval references, or switching programme details here.

Document Control

| Revision | Date | Description of Change | Author | Approved By |
| --- | --- | --- | --- | --- |
| A |  | Initial issue |  |  |