| LOOP CHECK RECORD SHEET |  |
| --- | --- |
| Document Ref: | Enter document reference |
| Loop Check No: | Enter unique loop check number |
| Revision: | Enter revision number |
| Date: | DD / MM / YYYY |
| Project Name: | Enter project name |
| Contract Number: | Enter contract number |
| Prepared By: | Name, position and company |
| Approved By: | Name, position and company |

This record documents the end-to-end loop check for an instrument loop from field device through cabling, junction boxes and marshalling to the PLC/SCADA I/O. A loop check verifies that the entire signal path is correct, continuous and producing the expected reading at the control system for a given simulated field input.

1. Loop Details

| Loop Tag Number: |  |
| --- | --- |
| Loop Description: | e.g. Wet well level indication and high level alarm |
| P&ID Reference: |  |
| Loop Drawing Reference: | Enter instrument loop diagram (ILD) number |
| System / Process: |  |
| Field Instrument Tag: |  |
| Field Instrument Type: | e.g. 4–20 mA pressure transmitter, RTD, flow meter, level switch |
| Field Instrument Make / Model: |  |
| Receiving Device (PLC / SCADA): | Enter PLC rack/slot/channel or SCADA point address |
| I/O Type: | AI / AO / DI / DO / RTD / TC / HART / Bus |
| Signal Type: | 4–20 mA / 0–10 V / Volt-free contact / Pulse / Digital / RTD |
| Cable Reference: | Enter cable number(s) in loop |
| Junction Box / Marshalling: | Enter JB or marshalling panel reference |
| Fuse / Isolator Reference: | Enter fuse or instrument isolator reference |

2. Loop Check Steps

Complete each step in sequence. Mark Done or N/A.

| No. | Loop Check Step | Done | N/A | Initials |
| --- | --- | --- | --- | --- |
| 1 | Loop drawing (ILD) reviewed and understood before commencing |  |  |  |
| 2 | Cable continuity verified end-to-end (all cores) |  |  |  |
| 3 | Cable insulation resistance (IR) tested and acceptable |  |  |  |
| 4 | Cable screens connected at one end only (as per specification) and insulated at far end |  |  |  |
| 5 | Cable terminations correct at field instrument end (verify against ILD) |  |  |  |
| 6 | Cable terminations correct at JB / marshalling panel (verify against ILD) |  |  |  |
| 7 | Cable terminations correct at PLC / DCS / SCADA I/O card (verify against ILD) |  |  |  |
| 8 | Instrument power supply present and correct voltage at field device |  |  |  |
| 9 | Loop power supply checked (24 V DC loop supply from I/O or barrier) |  |  |  |
| 10 | Intrinsic safety barrier installed and correct type (if IS loop) |  |  |  |
| 11 | Simulate 0% input at field — verify 4 mA / 0% reading at control system |  |  |  |
| 12 | Simulate 25% input at field — verify 8 mA / 25% reading at control system |  |  |  |
| 13 | Simulate 50% input at field — verify 12 mA / 50% reading at control system |  |  |  |
| 14 | Simulate 75% input at field — verify 16 mA / 75% reading at control system |  |  |  |
| 15 | Simulate 100% input at field — verify 20 mA / 100% reading at control system |  |  |  |
| 16 | Over-range checked (> 20.5 mA) — alarm or fail-safe response verified |  |  |  |
| 17 | Under-range checked (< 3.8 mA) — alarm or fail-safe response verified |  |  |  |
| 18 | Engineering units displayed correctly on SCADA / HMI |  |  |  |
| 19 | Alarm set points verified at control system (HH / H / L / LL as applicable) |  |  |  |
| 20 | Alarm annunciation verified on SCADA / HMI (correct tag, description, priority) |  |  |  |
| 21 | Digital input / output function verified (correct state for open/closed) |  |  |  |
| 22 | Analogue output tested (if control output — valve, VSD, actuator response verified) |  |  |  |
| 23 | Instrument label / tag plate verified in field |  |  |  |
| 24 | Loop fully functional end-to-end |  |  |  |

3. Simulation Results

Record the simulated input, expected signal, measured signal and SCADA/HMI reading at each test point.

| Simulated Input | Expected Signal | Measured Signal | SCADA Reading | Pass / Fail |
| --- | --- | --- | --- | --- |
| 0% |  |  |  |  |
| 25% |  |  |  |  |
| 50% |  |  |  |  |
| 75% |  |  |  |  |
| 100% |  |  |  |  |
| Over-range |  |  |  |  |
| Under-range |  |  |  |  |

4. Loop Check Result

| Loop Check Result: | PASS / FAIL |
| --- | --- |
| Defects / Snags Found: | Yes / No (describe) |
| Corrective Action: | Describe any rework or correction required |
| Recheck Required: | Yes / No |

5. Sign-Off

| Role | Print Name | Signature | Date |
| --- | --- | --- | --- |
| I&C Technician |  |  |  |
| I&C Engineer |  |  |  |
| SCADA / PLC Engineer |  |  |  |
| Commissioning Engineer |  |  |  |
| Client / Engineer's Representative |  |  |  |

6. Notes / Additional Comments

Enter any additional notes

7. Document Control

| Rev | Date | Description | Author | Approved |
| --- | --- | --- | --- | --- |

References: Instrument Loop Diagram (ILD), P&ID, Cable Schedule, SCADA Point Schedule, Project Specification, ITP