| PANEL WIRING INSPECTION CHECKLIST |  |
| --- | --- |
| Document Ref: | Enter document reference |
| Revision: | Enter revision number |
| Date: | DD / MM / YYYY |
| Project Name: | Enter project name |
| Contract Number: | Enter contract number |
| Panel Tag / Reference: | Enter MCC, PLC panel, LV switchboard, control panel ref |
| Panel Manufacturer: |  |
| Panel Serial Number: |  |
| Panel Drawing Reference: | Enter GA, schematic and wiring diagram references |
| Location: |  |
| Prepared By: | Name, position and company |
| Approved By: | Name, position and company |

This checklist documents the inspection of electrical panels, MCCs, control panels and switchboards. It covers external condition, internal wiring quality, and pre-energisation testing. Panels must comply with BS EN 61439 and BS 7671. This inspection must be completed before the panel is energised.

1. External Inspection

| No. | External Inspection | Done | N/A | Comments / Initials |
| --- | --- | --- | --- | --- |
| 1 | Panel enclosure undamaged (no dents, scratches exposing bare metal, corrosion) |  |  |  |
| 2 | Panel IP rating maintained (gaskets intact, all gland plates sealed, no unused openings) |  |  |  |
| 3 | Panel door hinges, catches and locks operational |  |  |  |
| 4 | Panel earthing stud / terminal present and accessible |  |  |  |
| 5 | Nameplate / data plate fitted with correct panel reference and rating |  |  |  |
| 6 | Danger and warning labels fitted (voltage, isolation, arc flash where required) |  |  |  |
| 7 | Panel mounted level, plumb and secure to support structure |  |  |  |
| 8 | Cable entry gland plates fitted with correct glands (sealed, labelled) |  |  |  |
| 9 | External isolator handle operational (if fitted) |  |  |  |
| 10 | Anti-condensation heater fitted and operational (if specified) |  |  |  |
| 11 | Ventilation fans and filters fitted and operational (if specified) |  |  |  |
| 12 | Panel lighting fitted and operational (door-operated switch) |  |  |  |

2. Internal Wiring Inspection

| No. | Internal Wiring Inspection | Done | N/A | Comments / Initials |
| --- | --- | --- | --- | --- |
| 13 | Internal wiring matches schematic / wiring diagram (point-to-point check) |  |  |  |
| 14 | All wire ferrules fitted with correct identification (per wiring diagram) |  |  |  |
| 15 | Wire ferrules legible and correctly orientated |  |  |  |
| 16 | All terminal connections tight (torqued to manufacturer specification) |  |  |  |
| 17 | No loose strands or exposed copper at terminal connections |  |  |  |
| 18 | Wire routing neat, dressed in trunking and secured with cable ties |  |  |  |
| 19 | Adequate bending radius maintained at all cable entries and connections |  |  |  |
| 20 | Wire colours correct per BS 7671 (brown L1, black L2, grey L3, blue N, green/yellow E) |  |  |  |
| 21 | DIN rail mounted components correctly positioned per layout drawing |  |  |  |
| 22 | All circuit breakers, contactors, relays and fuses correct type and rating per schedule |  |  |  |
| 23 | Overload relay settings verified against motor data (FLC marked on panel schedule) |  |  |  |
| 24 | All spare ways and terminals labelled as 'Spare' |  |  |  |
| 25 | All incoming and outgoing cables terminated per cable schedule |  |  |  |
| 26 | Cable screens terminated as per specification (single point earth where required) |  |  |  |
| 27 | Earth bus bar connections complete and tight |  |  |  |
| 28 | Neutral bus bar connections complete and tight (where applicable) |  |  |  |
| 29 | PLC / controller I/O module addresses verified against I/O schedule |  |  |  |
| 30 | PLC / controller power supply voltage correct and within tolerance |  |  |  |
| 31 | UPS (if fitted) operational and battery charged |  |  |  |
| 32 | Surge protection devices (SPDs) fitted where specified |  |  |  |

3. Testing and Functional Checks

| No. | Testing and Functional Checks | Done | N/A | Comments / Initials |
| --- | --- | --- | --- | --- |
| 33 | Insulation resistance (IR) test completed on all circuits within panel (pre-energisation) |  |  |  |
| 34 | Continuity of protective conductors verified |  |  |  |
| 35 | Phase rotation verified (for 3-phase panels) |  |  |  |
| 36 | Voltage present at correct level on all busbars / incoming supply (after energisation) |  |  |  |
| 37 | All circuit breakers trip tested (manual operation and overcurrent if applicable) |  |  |  |
| 38 | All contactors operate correctly (manual and from control circuit) |  |  |  |
| 39 | All relays operate correctly (function verified) |  |  |  |
| 40 | All indicator lamps and pilot lights operational and correct colour |  |  |  |
| 41 | Emergency stop function tested (all E-stops in loop verified) |  |  |  |
| 42 | Door interlock tested (if fitted — panel cannot be opened when live unless bypass key used) |  |  |  |
| 43 | All labels, circuit charts and operating instructions fitted inside panel door |  |  |  |

4. Overall Result

| Panel Inspection Result: | PASS / FAIL / Conditional (with snag list) |
| --- | --- |
| Snags / Defects Found: | Yes / No (list and NCR reference if applicable) |
| Panel Ready for Energisation: | Yes / No |
| FAT Certificate Reference: | Enter factory acceptance test certificate ref (if applicable) |

5. Sign-Off

| Role | Print Name | Signature | Date |
| --- | --- | --- | --- |
| Electrical Inspector / Engineer |  |  |  |
| Panel Manufacturer Representative |  |  |  |
| Commissioning Engineer |  |  |  |
| Quality Manager |  |  |  |
| Client / Engineer's Representative |  |  |  |

6. Notes / Additional Comments

Enter any additional notes

7. Document Control

| Rev | Date | Description | Author | Approved |
| --- | --- | --- | --- | --- |

References: BS EN 61439 (LV switchgear assemblies), BS 7671 (18th Edition), Panel Manufacturer Manual, Schematic Drawings, Project Specification, ITP