| RCD TRIP TEST RECORD |  |
| --- | --- |
| Document Ref: | Enter document reference |
| Revision: | Enter revision number |
| Date: | DD / MM / YYYY |
| Project Name: | Enter project name |
| Contract Number: | Enter contract number |
| Distribution Board / Panel: | Enter DB reference |
| Drawing Reference: | Enter SLD / circuit chart reference |
| Prepared By: | Name, position and company |
| Approved By: | Name, position and company |

This record documents RCD trip testing in accordance with BS 7671 Regulation 612.13. Each RCD must be tested at x0.5 rated residual current (to confirm no nuisance tripping), at x1 rated residual current (to confirm trip within maximum time), and at x5 rated residual current (to confirm fast disconnection). For S-type (time-delayed) RCDs, different limits apply. The integral test button must also be checked.

1. Test Equipment

| RCD Tester Make: |  |
| --- | --- |
| Model: |  |
| Serial Number: |  |
| Calibration Date: | DD / MM / YYYY |
| Calibration Certificate Ref: |  |

2. Maximum Trip Times (per BS EN 61008 / BS EN 61009)

| RCD Rating (mA) | At IΔn (max ms) | At 5xIΔn (max ms) | Type |
| --- | --- | --- | --- |
| 30 | 300 | 40 | General / AC / A / F / B |
| 100 | 300 | 40 | General |
| 300 | 300 | 40 | General |
| 30 (S type) | 500 (130-500) | 200 | Time-delayed (selective) |
| 100 (S type) | 500 (130-500) | 200 | Time-delayed (selective) |
| 300 (S type) | 500 (130-500) | 200 | Time-delayed (selective) |

3. RCD Trip Test Results

Test at 0.5x IΔn: confirm NO trip. Test at 1x IΔn: record trip time. Test at 5x IΔn: record trip time. Test at 0° and 180° phase angle for Type AC/A. Check integral test button operates.

| No. | RCD Ref / Location | Circuit(s) Protected | Rating mA | Type | x0.5 IΔn (no trip) | x1 IΔn (ms) | x5 IΔn (ms) | 0° (ms) | 180° (ms) | Test Button | Pass / Fail | Date | Tester |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 9 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 11 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 12 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 13 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 14 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 15 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 16 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 17 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 18 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 19 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 20 |  |  |  |  |  |  |  |  |  |  |  |  |  |

4. Sign-Off

| Role | Print Name | Signature | Date |
| --- | --- | --- | --- |
| Electrical Tester |  |  |  |
| Electrical Supervisor |  |  |  |
| Quality Manager |  |  |  |
| Client / Engineer's Representative |  |  |  |

5. Document Control

| Rev | Date | Description | Author | Approved |
| --- | --- | --- | --- | --- |

References: BS 7671 (18th Edition, Regulation 612.13), BS EN 61008 (RCCBs), BS EN 61009 (RCBOs), GN3 (IET Guidance Note 3), EIC / EICR, Project Specification