| DUCTWORK INSTALLATION AND LEAK TEST RECORD |  |
| --- | --- |
| Document Ref: | Enter document reference |
| Revision: | Enter revision number |
| Date: | DD / MM / YYYY |
| Project Name: | Enter project name |
| Contract Number: | Enter contract number |
| Prepared By: | Name, position and company |
| Approved By: | Name, position and company |

This record documents the installation inspection and air leakage testing of ductwork systems. Leak testing must be carried out in accordance with HVCA DW/144 (Specification for Sheet Metal Ductwork) and BS EN 12237. All ductwork must be tested before insulation is applied. The maximum allowable leakage depends on the ductwork pressure class.

1. System Details

| System / AHU Reference: |  |
| --- | --- |
| System Description: | e.g. Supply air, extract air, fresh air, recirculation, fume extract, kitchen extract, smoke extract |
| Drawing Reference: | Enter ductwork layout drawing and schematic |
| Specification Reference: | Enter spec clause (DW/144, DW/143, HVCA/DW/172, CIBSE) |
| Ductwork Material: | Galvanised steel / Stainless steel / Aluminium / PVC / GRP / Phenolic board / Flexible |
| Ductwork Pressure Class: | Low pressure (Class A) / Medium pressure (Class B) / High pressure (Class C/D) |
| Ductwork Leakage Class: | Class A / B / C / D (per BS EN 12237 / DW/144) |
| Maximum Allowable Leakage Rate: | Enter l/s per m² duct surface area (per DW/144 Table) |
| System Operating Pressure (Pa): |  |
| Test Section Reference: | Enter test section identifier |
| Test Section Surface Area (m²): |  |
| Test Section Length (m): |  |
| Location / Zone: |  |

2. Installation Checklist

| No. | Installation Check | Done | N/A | Comments |
| --- | --- | --- | --- | --- |
| 1 | Ductwork installed per layout drawing (routing, sizes, orientation confirmed) |  |  |  |
| 2 | All joints correctly made — flanged, slip, clipped or welded per specification |  |  |  |
| 3 | Joint sealant applied to all transverse and longitudinal joints (DW/144 requirement) |  |  |  |
| 4 | Ductwork adequately supported — hangers, brackets and trapeze at correct centres |  |  |  |
| 5 | Ductwork support spacing within specification (max centres per DW/144 Table 4.4) |  |  |  |
| 6 | Flexible connections installed at fan and equipment connections (to prevent vibration transmission) |  |  |  |
| 7 | Fire dampers installed at all fire compartment penetrations (correct orientation, access panels provided) |  |  |  |
| 8 | Volume control dampers installed per drawing and accessible for adjustment |  |  |  |
| 9 | Access panels / doors installed at all inspection points, fire dampers and cleaning positions |  |  |  |
| 10 | Ductwork cleaned internally before sealing (no construction debris, dust, swarf) |  |  |  |
| 11 | All open duct ends capped / sealed during construction to prevent contamination |  |  |  |
| 12 | Ductwork insulation installed where specified (thermal and/or acoustic) |  |  |  |
| 13 | Insulation vapour barrier intact and sealed at joints (condensation prevention) |  |  |  |
| 14 | Diffusers, grilles and terminal devices installed per drawing (correct type and size) |  |  |  |
| 15 | Ductwork identified / labelled per system reference (colour coding or labels per BSRIA BG 29) |  |  |  |
| 16 | Smoke extract ductwork rated to correct standard (BS EN 12101-7 / BS 476) |  |  |  |
| 17 | Kitchen extract ductwork constructed to DW/172 (grease extract specification) |  |  |  |

3. Leak Test Record

Record the leak test results for each test section.

| Test Method: | Pressure decay / Orifice plate / Flow measurement |
| --- | --- |
| Test Equipment: | Fan, manometer, orifice plate — make, model, calibration date |
| Test Pressure (Pa): | Enter test pressure per DW/144 (typically 400 Pa for Class A, 1000 Pa for Class B, etc.) |
| Measured Leakage Rate (l/s): |  |
| Duct Surface Area of Test Section (m²): |  |
| Measured Leakage Rate per m² (l/s/m²): | Divide total leakage by surface area |
| Maximum Allowable Leakage (l/s/m²): | Enter per DW/144 Table for the pressure class |
| Test Duration (minutes): |  |
| Leaks Identified During Test: | Yes / No (if Yes, describe location and remedial action) |
| Remedial Action Taken: | Re-sealed joints / Replaced section / Applied additional sealant |
| Retest Required: | Yes / No |
| Retest Result: | Pass / Fail / N/A |
| Overall Test Result: | PASS — Within allowable leakage / FAIL — Exceeds allowable leakage |

4. Sign-Off

By signing, each party confirms the ductwork has been installed and tested in accordance with the specification.

| Role | Print Name | Signature | Date |
| --- | --- | --- | --- |
| Ductwork Installer / Supervisor |  |  |  |
| M&E Engineer |  |  |  |
| Commissioning Engineer |  |  |  |
| Quality Manager |  |  |  |
| Client / Engineer's Representative |  |  |  |

5. Notes / Additional Comments

Enter any additional notes

6. Document Control

| Rev | Date | Description of Change | Author | Approved By |
| --- | --- | --- | --- | --- |

References: HVCA DW/144, DW/143, DW/172 (kitchen extract), BS EN 12237, BS EN 1507, BS EN 12101-7 (smoke extract), CIBSE Guide B, BSRIA BG 29, Project Specification, ITP