| PUMP INSTALLATION RECORD SHEET |  |
| --- | --- |
| Document Ref: | Enter document reference |
| Revision: | Enter revision number |
| Date: | DD / MM / YYYY |
| Project Name: | Enter project name |
| Contract Number: | Enter contract number |
| Prepared By: | Name, position and company |
| Approved By: | Name, position and company |

This record documents the installation of each pump on the project. It covers pump and motor details, mechanical and electrical installation checks, and coupling alignment. This record must be completed before the pump is commissioned.

1. Pump Details

| Pump Tag Number: |  |
| --- | --- |
| P&ID Reference: |  |
| Pump Type: | Centrifugal / Submersible / Positive displacement / Screw / Diaphragm / Peristaltic / Other |
| Manufacturer: |  |
| Model: |  |
| Serial Number: |  |
| Impeller Diameter (mm): |  |
| Design Flow (l/s or m³/hr): |  |
| Design Head (m): |  |
| Speed (rpm): |  |
| Power (kW): |  |
| Duty Point: | State flow and head at duty point |
| Media / Fluid: | Describe fluid pumped |
| Seal Type: | Mechanical seal / Packed gland / Lip seal / Mag drive / Other |
| Bearing Type: |  |
| Weight (kg): |  |
| Installation Drawing Ref: |  |

2. Motor Details

| Motor Tag Number: |  |
| --- | --- |
| Manufacturer: |  |
| Frame Size: |  |
| Rated Power (kW): |  |
| Rated Voltage (V): |  |
| Full Load Current (A): |  |
| Speed (rpm): |  |
| Enclosure (IP Rating): | IP55 / IP56 / IP68 / Other |
| Insulation Class: | B / F / H |
| Motor Serial Number: |  |

3. Mechanical Installation Checklist

| No. | Mechanical Installation | Done | N/A | Comments / Initials |
| --- | --- | --- | --- | --- |
| 1 | Foundation / plinth level and alignment checked and within tolerance |  |  |  |
| 2 | Holding-down bolts tightened to specification and torqued |  |  |  |
| 3 | Pump and motor set on baseplate, aligned and levelled |  |  |  |
| 4 | Baseplate grouted (non-shrink grout) and cured |  |  |  |
| 5 | Suction pipework connected, supported and free from stress on pump casing |  |  |  |
| 6 | Discharge pipework connected, supported and free from stress on pump casing |  |  |  |
| 7 | Eccentric reducer fitted on suction (flat side up for horizontal pump) |  |  |  |
| 8 | Isolation valves installed and accessible (suction and discharge) |  |  |  |
| 9 | Non-return valve installed on discharge (correct orientation) |  |  |  |
| 10 | Pressure gauge tappings installed (suction and discharge) |  |  |  |
| 11 | Drain and vent connections made |  |  |  |
| 12 | Seal water / flush water connections made (if applicable) |  |  |  |
| 13 | Pump primed and suction pipe filled (no air locks) |  |  |  |
| 14 | Coupling alignment completed — laser / dial gauge readings within tolerance |  |  |  |
| 15 | Coupling guard fitted and secure |  |  |  |
| 16 | All fasteners tightened and lock-wired or tabbed where required |  |  |  |
| 17 | Lubrication completed per manufacturer requirements (grease / oil) |  |  |  |
| 18 | Cooling system connected (if applicable) |  |  |  |

4. Electrical Installation Checklist

| No. | Electrical Installation | Done | N/A | Comments / Initials |
| --- | --- | --- | --- | --- |
| 19 | Motor IR test completed and recorded (Megger reading acceptable) |  |  |  |
| 20 | Motor rotation checked by bump test (correct direction confirmed) |  |  |  |
| 21 | Electrical connections complete, tightened and insulated |  |  |  |
| 22 | Earth bonding connected and tested |  |  |  |
| 23 | Motor protection relay / overload set to correct FLC |  |  |  |
| 24 | VSD / soft starter parameters set (if applicable) |  |  |  |
| 25 | Emergency stop tested and operational |  |  |  |
| 26 | Local isolator operational and lockable |  |  |  |
| 27 | Control wiring complete and loop checked |  |  |  |
| 28 | Motor heaters energised (anti-condensation) |  |  |  |

5. Coupling Alignment Record

Record alignment readings. Alignment must be within manufacturer's tolerance.

| Alignment Method: | Laser / Dial gauge (rim and face) / Straight edge (rough) |
| --- | --- |
| Horizontal Angularity: | Enter mm/100mm or mils |
| Vertical Angularity: | Enter mm/100mm or mils |
| Horizontal Offset: | Enter mm or mils |
| Vertical Offset: | Enter mm or mils |
| Tolerance (manufacturer): | Enter acceptable values |
| Alignment Result: | Within tolerance / Out of tolerance (shimmed and rechecked) |
| Alignment Report Ref: | Enter laser alignment report reference if available |

6. Sign-Off

By signing, each discipline confirms installation is complete and the pump is ready for commissioning.

| Role | Print Name | Signature | Date |
| --- | --- | --- | --- |
| Mechanical Engineer / Fitter |  |  |  |
| Electrical Engineer |  |  |  |
| Commissioning Engineer |  |  |  |
| Quality Manager |  |  |  |
| Client / Engineer's Representative |  |  |  |

7. Notes / Additional Comments

Enter any additional notes

8. Document Control

| Rev | Date | Description of Change | Author | Approved By |
| --- | --- | --- | --- | --- |

References: Manufacturer's Installation Manual, BS EN ISO 5199 (technical specifications for centrifugal pumps), BS EN 809, Hydraulic Institute Standards, Project Specification, ITP