| CONTINUITY TEST RECORD |  |
| --- | --- |
| Document Ref: | Enter document reference |
| Revision: | Enter revision number |
| Date: | DD / MM / YYYY |
| Project Name: | Enter project name |
| Contract Number: | Enter contract number |
| System / DB Reference: | Enter distribution board or system reference |
| Drawing Reference: | Enter SLD / circuit chart reference |
| Prepared By: | Name, position and company |
| Approved By: | Name, position and company |

This record documents continuity testing of protective conductors and bonding conductors in accordance with BS 7671 Regulation 612.2. The R1+R2 values are used to verify that the earth fault loop impedance (Zs) will be low enough to ensure protective devices operate within the required disconnection time. Bonding continuity must also be verified.

1. Test Equipment

| Low Resistance Ohmmeter Make: |  |
| --- | --- |
| Model: |  |
| Serial Number: |  |
| Calibration Date: | DD / MM / YYYY |
| Calibration Certificate Ref: |  |
| Test Lead Resistance (null reading): | Enter Ω (to be subtracted from readings) |

2. Protective Conductor Continuity (R1+R2)

Measure R1+R2 for each circuit. Correct to 20°C if ambient differs significantly. Calculated Zs = Ze + (R1+R2 corrected). Compare with maximum Zs from BS 7671 tables.

| No. | Circuit Ref | Circuit Description | Cable Size mm² | Length m | R1 Ω | R2 Ω | R1+R2 Ω | R1+R2 Corrected Ω | Zs Calc Ω | Max Zs Ω | Pass/Fail | Tester |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |  |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |  |  |  |  |  |  |
| 6 |  |  |  |  |  |  |  |  |  |  |  |  |
| 7 |  |  |  |  |  |  |  |  |  |  |  |  |
| 8 |  |  |  |  |  |  |  |  |  |  |  |  |
| 9 |  |  |  |  |  |  |  |  |  |  |  |  |
| 10 |  |  |  |  |  |  |  |  |  |  |  |  |
| 11 |  |  |  |  |  |  |  |  |  |  |  |  |
| 12 |  |  |  |  |  |  |  |  |  |  |  |  |
| 13 |  |  |  |  |  |  |  |  |  |  |  |  |
| 14 |  |  |  |  |  |  |  |  |  |  |  |  |
| 15 |  |  |  |  |  |  |  |  |  |  |  |  |
| 16 |  |  |  |  |  |  |  |  |  |  |  |  |
| 17 |  |  |  |  |  |  |  |  |  |  |  |  |
| 18 |  |  |  |  |  |  |  |  |  |  |  |  |
| 19 |  |  |  |  |  |  |  |  |  |  |  |  |
| 20 |  |  |  |  |  |  |  |  |  |  |  |  |
| 21 |  |  |  |  |  |  |  |  |  |  |  |  |
| 22 |  |  |  |  |  |  |  |  |  |  |  |  |
| 23 |  |  |  |  |  |  |  |  |  |  |  |  |
| 24 |  |  |  |  |  |  |  |  |  |  |  |  |
| 25 |  |  |  |  |  |  |  |  |  |  |  |  |

3. Bonding Conductor Continuity

Verify continuity of main protective bonding and supplementary bonding conductors.

| No. | Bonding Conductor From | To | Conductor Size mm² | Resistance Ω | Max Allowed Ω | Pass/Fail |
| --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |
| 6 |  |  |  |  |  |  |
| 7 |  |  |  |  |  |  |
| 8 |  |  |  |  |  |  |
| 9 |  |  |  |  |  |  |
| 10 |  |  |  |  |  |  |

4. Sign-Off

| Role | Print Name | Signature | Date |
| --- | --- | --- | --- |
| Electrical Tester |  |  |  |
| Electrical Supervisor |  |  |  |
| Quality Manager |  |  |  |
| Client / Engineer's Representative |  |  |  |

5. Document Control

| Rev | Date | Description | Author | Approved |
| --- | --- | --- | --- | --- |

References: BS 7671 (18th Edition, Regulation 612.2), GN3 (IET Guidance Note 3), BS 7671 Tables 41.2-41.4 (max Zs), EIC / EICR, Project Specification, ITP