Hot Works Fire Watch Checklist

Health & Safety – Fire Safety

| Document Ref: | Enter document reference |
| --- | --- |
| Revision: | Enter revision number |
| Date: | DD / MM / YYYY |
| Project Name: | Enter project name |
| Contract No: | Enter contract number |
| Prepared By: | Enter name and role |
| Approved By: | Enter name and role |

# Hot Works Details

| Hot Works Permit No: | Enter the permit number |
| --- | --- |
| Type of Hot Works: | e.g. Welding, oxy-fuel cutting, grinding, brazing, soldering, bitumen heating |
| Location of Works: | Enter exact location on site |
| Date of Works: | DD / MM / YYYY |
| Planned Start Time: | HH:MM |
| Planned Finish Time: | HH:MM |
| Hot Works Operative: | Enter name and company |
| Fire Watch Person: | Enter name and company |
| Permit Issued By: | Enter name and role |

# Pre-Work Fire Safety Checklist

All items must be checked and confirmed before hot works commence. If any item is marked ‘No’, the issue must be resolved before work can start. Do not commence hot works until all applicable items are confirmed.

| No. | Pre-Work Check | Yes | No | N/A | Initials |
| --- | --- | --- | --- | --- | --- |
| 1 | Valid hot works permit obtained and displayed at the work area |  |  |  |  |
| 2 | Risk assessment and method statement reviewed and briefed |  |  |  |  |
| 3 | All combustible materials removed or protected within a minimum radius of 10 metres |  |  |  |  |
| 4 | Flammable liquids, gases and vapours eliminated from the work area |  |  |  |  |
| 5 | Floor swept clean of sawdust, shavings, paper and other combustible debris |  |  |  |  |
| 6 | Gaps, holes and openings in floors and walls sealed or protected to prevent spread of sparks |  |  |  |  |
| 7 | Combustible wall and ceiling linings protected with fire-resistant sheeting or screens |  |  |  |  |
| 8 | Fire-resistant screens / welding curtains erected to contain sparks and spatter |  |  |  |  |
| 9 | Adjacent rooms, areas above and below checked for combustible materials |  |  |  |  |
| 10 | Fire detection and suppression systems in the area operational (or isolated with approval) |  |  |  |  |
| 11 | Suitable fire extinguisher(s) immediately available at the work location (minimum 2 x CO2 or dry powder) |  |  |  |  |
| 12 | Fire watch person designated and briefed on their duties |  |  |  |  |
| 13 | Fire watch person has unobstructed access to fire alarm activation point |  |  |  |  |
| 14 | Smoke detection equipment in the area has been considered (temporary isolation if necessary with approval) |  |  |  |  |
| 15 | Hot works operative confirmed competent (relevant qualifications checked) |  |  |  |  |
| 16 | Adequate ventilation provided for the task |  |  |  |  |
| 17 | Gas cylinders secured upright, valves accessible, flashback arrestors fitted |  |  |  |  |
| 18 | Hoses and connections checked for damage and tightness |  |  |  |  |
| 19 | No other hot works in the vicinity that could create cumulative fire risk |  |  |  |  |
| 20 | Emergency evacuation route clear and unobstructed |  |  |  |  |

# Fire Watch Monitoring During Works

The fire watch person must continuously monitor the work area during hot works. Record periodic checks below.

| No. | Monitoring Check | Yes | No | N/A | Initials |
| --- | --- | --- | --- | --- | --- |
| 1 | Fire watch commenced at start of hot works |  |  |  |  |
| 2 | Work area continuously observed for signs of fire, smouldering or smoke |  |  |  |  |
| 3 | Regular checks of adjacent areas, below and above the work zone |  |  |  |  |
| 4 | Fire extinguisher(s) remain immediately accessible and not obstructed |  |  |  |  |
| 5 | No combustible materials have been introduced to the exclusion zone |  |  |  |  |
| 6 | Ventilation remains adequate |  |  |  |  |
| 7 | Hot works operative is working safely and within permitted area |  |  |  |  |
| 8 | Any sparks or slag contained within fire-resistant screens |  |  |  |  |

# Post-Work Fire Watch Record

A fire watch must be maintained for a minimum of 60 minutes after the completion of hot works (or as specified by the hot works permit). The fire watch person must remain in the area, monitor for signs of fire and record their checks below.

| Hot Works Completed At: | HH:MM |
| --- | --- |
| Post-Work Fire Watch Duration: | Minimum 60 minutes (or as per permit) |
| Fire Watch End Time: | HH:MM |

| Check Time | Check No. | Observations (any signs of fire, heat, smoke?) | Fire Watch Initials |
| --- | --- | --- | --- |
| +10 min | 1 |  |  |
| +20 min | 2 |  |  |
| +30 min | 3 |  |  |
| +40 min | 4 |  |  |
| +50 min | 5 |  |  |
| +60 min | 6 |  |  |
| +90 min (if req.) | 7 |  |  |
| +120 min (if req.) | 8 |  |  |

# Final Area Inspection and Sign-Off

After the post-work fire watch period has elapsed, complete the final area inspection below.

| No. | Final Check | Yes | No | Initials |
| --- | --- | --- | --- | --- |
| 1 | Work area thoroughly inspected – no signs of fire, smouldering or smoke |  |  |  |
| 2 | Adjacent areas, above and below, checked – no signs of fire |  |  |  |
| 3 | All hot works equipment removed or made safe |  |  |  |
| 4 | Gas cylinders turned off and secured |  |  |  |
| 5 | Fire extinguishers returned to their designated locations |  |  |  |
| 6 | Fire detection systems reinstated (if previously isolated) |  |  |  |
| 7 | Combustible materials may be returned to the area |  |  |  |
| 8 | Area declared safe and fire watch concluded |  |  |  |

# Fire Watch Person Declaration

I confirm that I have carried out the fire watch duties as described above, maintained continuous observation during and after hot works, and that the area has been inspected and declared safe at the conclusion of the fire watch period.

| Name: |  | Date: |  |
| --- | --- | --- | --- |
| Signature: |  | Time: |  |

# Supervisor / Permit Issuer Confirmation

| Name: |  | Date: |  |
| --- | --- | --- | --- |
| Signature: |  | Role: |  |

# Notes / Additional Comments

Enter any additional notes or comments here.

# Document Control

| Revision | Date | Description of Change | Author | Approved By |
| --- | --- | --- | --- | --- |