SAT Commissioning Checklist

Site Acceptance Test — System Commissioning Verification and Sign-Off Record

| Project and SAT Details |  |  |  |
| --- | --- | --- | --- |
| Document Ref: |  | Revision: |  |
| Project Name: |  | Contract No: |  |
| Site / Plant: |  | System / Area: | e.g., inlet works, chemical dosing, MCC-01 |
| SAT Date: | DD/MM/YYYY | FAT Reference (if completed): |  |
| SAT Procedure Ref: |  | SAT Procedure Rev: |  |
| Contractor: |  | Client: |  |
| Commissioning Engineer: |  | Client Witness: |  |

1. SAT Prerequisites

| A: Pre-SAT Requirements |  |  |  |  |
| --- | --- | --- | --- | --- |
| No. | Item | Y | N | Comments / Evidence |
| 1 | FAT completed and all FAT punch list items closed out (or deferred with agreement) |  |  |  |
| 2 | All construction and installation works complete for the system under test |  |  |  |
| 3 | Mechanical completion certificate issued for the system |  |  |  |
| 4 | All electrical installations tested and certified (BS 7671 test certificates available) |  |  |  |
| 5 | All instrument loop checks completed and signed off |  |  |  |
| 6 | All point-to-point wiring checks completed |  |  |  |
| 7 | Control system software loaded and at the correct revision |  |  |  |
| 8 | SCADA / HMI graphics loaded and at the correct revision |  |  |  |
| 9 | Network infrastructure tested (communications, fibre, switches, IP addressing) |  |  |  |
| 10 | All safety systems / interlocks tested and verified (SIL tested if applicable) |  |  |  |
| 11 | All relevant documentation available on site (O&M manuals, drawings, data sheets) |  |  |  |
| 12 | Risk assessment and method statement for SAT activities approved |  |  |  |
| 13 | Safe system of work in place for live testing (permits, isolations, briefings) |  |  |  |

2. Hardware and Installation Checks

| B: Hardware Verification |  |  |  |  |
| --- | --- | --- | --- | --- |
| No. | Item | Y | N | Comments / Evidence |
| 1 | Control panel(s) installed, labelled, and clean |  |  |  |
| 2 | PLC / controller powered up and running with no hardware faults |  |  |  |
| 3 | All I/O modules present, correctly addressed, and status LEDs normal |  |  |  |
| 4 | UPS (if fitted) operational with correct battery charge status |  |  |  |
| 5 | HMI / operator panel(s) powered up and displaying correctly |  |  |  |
| 6 | Network switches, routers, and communications equipment operational |  |  |  |
| 7 | All field instruments reading live values (no fault flags) |  |  |  |
| 8 | All motor starters / VSDs powered and ready (no trip conditions) |  |  |  |
| 9 | All control valves / actuators responding to commands |  |  |  |
| 10 | Emergency stop circuits tested and operational at all E-stop locations |  |  |  |

3. Software and Functional Testing

| C: Control System Functional Tests |  |  |  |  |
| --- | --- | --- | --- | --- |
| No. | Item | Y | N | Comments / Evidence |
| 1 | PLC program version matches approved SAT version |  |  |  |
| 2 | SCADA software version matches approved SAT version |  |  |  |
| 3 | All analogue inputs reading correctly and within calibration |  |  |  |
| 4 | All digital inputs operating correctly (state changes verified) |  |  |  |
| 5 | All analogue outputs driving correctly to field devices |  |  |  |
| 6 | All digital outputs operating correctly (field device response verified) |  |  |  |
| 7 | Auto / manual control mode switching tested for all loops |  |  |  |
| 8 | PID control loops tuned and stable under process conditions |  |  |  |
| 9 | Setpoint changes tracked correctly by all control loops |  |  |  |
| 10 | All sequencing / batch control logic tested per the functional design specification (FDS) |  |  |  |
| 11 | Duty / standby changeover logic tested |  |  |  |
| 12 | Timer and counter functions verified |  |  |  |

4. Alarm and Event Management

| D: Alarms, Events, and Logging |  |  |  |  |
| --- | --- | --- | --- | --- |
| No. | Item | Y | N | Comments / Evidence |
| 1 | All process alarms configured and tested (high, low, high-high, low-low) |  |  |  |
| 2 | Alarm priorities correctly assigned per alarm philosophy document |  |  |  |
| 3 | Alarm annunciation correct on SCADA / HMI (visual and audible) |  |  |  |
| 4 | Alarm acknowledge and reset functions working correctly |  |  |  |
| 5 | Event logging operational — events recorded with correct timestamp |  |  |  |
| 6 | Historical data logging (trend recording) operational and storing data |  |  |  |
| 7 | Data archive / historian collecting data at correct intervals |  |  |  |
| 8 | Report generation tested (daily, weekly, monthly reports as specified) |  |  |  |

5. Safety Systems and Interlocks

| E: Safety and Interlocks |  |  |  |  |
| --- | --- | --- | --- | --- |
| No. | Item | Y | N | Comments / Evidence |
| 1 | All safety interlocks tested per the cause and effect matrix |  |  |  |
| 2 | Emergency shutdown (ESD) sequence tested end-to-end |  |  |  |
| 3 | Safety instrumented functions (SIF) tested per SIL requirements |  |  |  |
| 4 | Permissive / enable conditions verified for each equipment start |  |  |  |
| 5 | Trip and shutdown sequences operate within required time limits |  |  |  |
| 6 | Reset and restart procedures verified after trip condition |  |  |  |
| 7 | Fire detection and suppression interface tested (if applicable) |  |  |  |
| 8 | Gas detection system interface tested (if applicable) |  |  |  |

6. Communications and Integration

| F: Communications |  |  |  |  |
| --- | --- | --- | --- | --- |
| No. | Item | Y | N | Comments / Evidence |
| 1 | PLC-to-SCADA communication verified (all data points mapped correctly) |  |  |  |
| 2 | PLC-to-PLC communication tested (inter-controller data exchange) |  |  |  |
| 3 | Modbus / Profibus / Profinet / Ethernet/IP communication verified to field devices |  |  |  |
| 4 | HART communication to smart instruments verified |  |  |  |
| 5 | Remote access / VPN connection tested (if specified) |  |  |  |
| 6 | Telemetry / outstations communicating correctly (if applicable) |  |  |  |
| 7 | Printer / report output tested |  |  |  |
| 8 | Clock synchronisation (NTP / GPS time sync) verified across all systems |  |  |  |

7. SAT Test Schedule Summary

Record the outcome of each SAT test case. Reference the SAT procedure for detailed test steps.

| Test No. | Test Description | Expected Result | Actual Result | Pass / Fail | Comments / Snag Ref |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |
| 8 |  |  |  |  |  |
| 9 |  |  |  |  |  |
| 10 |  |  |  |  |  |
| 11 |  |  |  |  |  |
| 12 |  |  |  |  |  |
| 13 |  |  |  |  |  |
| 14 |  |  |  |  |  |
| 15 |  |  |  |  |  |

8. SAT Punch List / Snag List

| No. | Priority | Description | Assigned To | Target Date | Status |
| --- | --- | --- | --- | --- | --- |
| 1 | A / B / C |  |  | DD/MM/YYYY | Open / Closed |
| 2 | A / B / C |  |  | DD/MM/YYYY | Open / Closed |
| 3 | A / B / C |  |  | DD/MM/YYYY | Open / Closed |
| 4 | A / B / C |  |  | DD/MM/YYYY | Open / Closed |
| 5 | A / B / C |  |  | DD/MM/YYYY | Open / Closed |
| 6 | A / B / C |  |  | DD/MM/YYYY | Open / Closed |
| 7 | A / B / C |  |  | DD/MM/YYYY | Open / Closed |
| 8 | A / B / C |  |  | DD/MM/YYYY | Open / Closed |

9. Overall SAT Result

| SAT Status | PASS / CONDITIONAL PASS / FAIL |
| --- | --- |
| Conditions (if conditional): | List any outstanding items that must be resolved |

10. SAT Sign-Off

By signing below, we confirm that the Site Acceptance Test has been conducted in accordance with the approved SAT procedure and the results are as recorded in this document.

| Role | Name | Signature | Date |
| --- | --- | --- | --- |
| Commissioning Engineer |  |  | DD/MM/YYYY |
| ICA Supervisor |  |  | DD/MM/YYYY |
| Contractor Project Manager |  |  | DD/MM/YYYY |
| Client Representative |  |  | DD/MM/YYYY |
| Operations Representative |  |  | DD/MM/YYYY |

11. Notes / Additional Comments

Record additional observations, software version references, or deferred items.

12. Document Control

| Rev | Date | Description | Author | Approved |
| --- | --- | --- | --- | --- |
| 0 |  | Initial issue |  |  |
| 1 |  |  |  |  |