BS 7671 Test Certificate

Electrical Installation Certificate — Inspection and Test Results per BS 7671 (IET Wiring Regulations)

This certificate is a project-level record template for recording electrical inspection and test results. It does not replace the formal EIC/EICR issued by a registered competent person under an applicable scheme (e.g., NICEIC, NAPIT, ELECSA).

| Part 1: Details of the Installation |  |  |  |
| --- | --- | --- | --- |
| Certificate Ref: |  | Date: | DD/MM/YYYY |
| Project Name: |  | Contract No: |  |
| Installation Address: |  |  |  |
| Description of Installation: | e.g., new electrical installation, extension, alteration |  |  |
| Extent of Installation Covered: | e.g., entire installation, distribution board DB1 only |  |  |
| Date of Inspection: | DD/MM/YYYY | Date of Testing: | DD/MM/YYYY |
| Next Inspection Due: | DD/MM/YYYY | Inspection Interval: | e.g., 5 years |

Part 2: Details of the Contractor

| Contractor Name: |  |  |  |
| --- | --- | --- | --- |
| Address: |  |  |  |
| Telephone: |  | Email: |  |
| Registration Body: | e.g., NICEIC, NAPIT, ELECSA | Registration No: |  |
| Competent Person Name: |  | Qualification: | e.g., City & Guilds 2391, AM2 |

Part 3: Supply Characteristics and Earthing Arrangements

| System Type (TN-S, TN-C-S, TT, IT): |  | Supply Protective Device: | e.g., 100A BS 1361 fuse |
| --- | --- | --- | --- |
| Number of Phases: | e.g., single phase, three phase | Nominal Voltage (V): | e.g., 230V, 400V |
| Nominal Frequency (Hz): | 50 | Prospective Fault Current (kA): | at origin |
| External Earth Fault Loop (Ze): | ohms | Supply PEN/Earth Conductor: | e.g., PME, SNE, electrode |
| Main Switch / Isolator Rating: | amps | Main Switch BS / EN No: |  |
| Main Earthing Conductor Size: | mm2 | Main Bonding Conductor Size: | mm2 |
| Earth Electrode Resistance (RA): | ohms (TT systems) | Method of Measurement: |  |

Part 4: Circuit Test Results Schedule

Record the test results for each circuit. Reference BS 7671 Part 6 and GN3 (IET Guidance Note 3). All values must be within the limits specified in the Wiring Regulations.

| Cct No. | Circuit Description | Rating (A) | Type (B/C/D) | Cable Size (mm2) | Zs (ohms) | Max Zs (ohms) | IR (MOhms) | RCD Trip (ms) | R1+R2 (ohms) | Polarity OK | Pass / Fail |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |  |  |  |  |  |
| 6 |  |  |  |  |  |  |  |  |  |  |  |
| 7 |  |  |  |  |  |  |  |  |  |  |  |
| 8 |  |  |  |  |  |  |  |  |  |  |  |
| 9 |  |  |  |  |  |  |  |  |  |  |  |
| 10 |  |  |  |  |  |  |  |  |  |  |  |
| 11 |  |  |  |  |  |  |  |  |  |  |  |
| 12 |  |  |  |  |  |  |  |  |  |  |  |
| 13 |  |  |  |  |  |  |  |  |  |  |  |
| 14 |  |  |  |  |  |  |  |  |  |  |  |
| 15 |  |  |  |  |  |  |  |  |  |  |  |
| 16 |  |  |  |  |  |  |  |  |  |  |  |
| 17 |  |  |  |  |  |  |  |  |  |  |  |
| 18 |  |  |  |  |  |  |  |  |  |  |  |
| 19 |  |  |  |  |  |  |  |  |  |  |  |
| 20 |  |  |  |  |  |  |  |  |  |  |  |

Part 5: Insulation Resistance Summary

| Test | Test Voltage (V) | Result (MOhms) | Min. Acceptable |
| --- | --- | --- | --- |
| Live to Earth (L-E) | 500 |  | 1.0 |
| Live to Neutral (L-N) | 500 |  | 1.0 |
| Neutral to Earth (N-E) | 500 |  | 1.0 |
| SELV / PELV circuits (if applicable) | 250 |  | 0.5 |

Part 6: RCD Test Results

| RCD Location / Ref | Rated Residual (mA) | Type (AC/A/B) | Operating Time @ 1x (ms) | Operating Time @ 5x (ms) | Test Button OK | Ramp Test (mA) | Pass / Fail |
| --- | --- | --- | --- | --- | --- | --- | --- |

Part 7: Continuity of Protective Conductors

| Test | Result (ohms) | Acceptable | Pass / Fail |
| --- | --- | --- | --- |
| Main earth continuity |  | < 0.05 |  |
| Main bonding — gas |  | < 0.05 |  |
| Main bonding — water |  | < 0.05 |  |
| Main bonding — other (specify) |  | < 0.05 |  |
| Supplementary bonding (where required) |  | As per Reg. 415.2 |  |

Part 8: Overall Assessment

| Installation Condition | SATISFACTORY / UNSATISFACTORY |
| --- | --- |
| Observations / Limitations: | Record any observations, departures, or limitations |

Part 9: Certification Sign-Off

I/we being the person(s) responsible for the inspection and testing of the electrical installation, certify that the work does not impair the safety of the existing installation and that the installation has been designed, constructed, inspected, and tested in accordance with BS 7671 (IET Wiring Regulations) current edition.

| Role | Name | Signature | Date |
| --- | --- | --- | --- |
| Designer |  |  | DD/MM/YYYY |
| Installer |  |  | DD/MM/YYYY |
| Inspector / Tester |  |  | DD/MM/YYYY |
| Client / Duty Holder |  |  | DD/MM/YYYY |

Part 10: Notes / Additional Comments

Record any additional observations, departures from BS 7671, or items requiring attention.

Document Control

| Rev | Date | Description | Author | Approved |
| --- | --- | --- | --- | --- |
| 0 |  | Initial issue |  |  |
| 1 |  |  |  |  |