Loop Check Record

ICA Instrumentation — Instrument Loop Verification and Commissioning Record

| Project and Loop Details |  |  |  |
| --- | --- | --- | --- |
| Document Ref: |  | Revision: |  |
| Project Name: |  | Contract No: |  |
| Site / Plant: |  | System / Area: |  |
| Loop Check Date: | DD/MM/YYYY | Sheet ___ of ___: |  |
| Contractor: |  | Client: |  |
| Checked By: |  | Witnessed By: |  |

1. Loop Identification

| Loop Tag Number: | e.g., FIT-101, LT-205, PT-302 | Loop Description: | e.g., raw water flow, sludge tank level |
| --- | --- | --- | --- |
| P&ID Reference: |  | P&ID Revision: |  |
| Loop Drawing Reference: |  | Cable Schedule Ref: |  |
| Signal Type: | e.g., 4-20mA, 0-10V, HART, digital, Modbus | SIL Rating (if applicable): | e.g., SIL 1, SIL 2 |
| Control System: | e.g., PLC, SCADA, DCS — tag in system |  |  |

2. Field Instrument Details

| Instrument Tag: |  | Service: |  |
| --- | --- | --- | --- |
| Manufacturer: |  | Model: |  |
| Serial Number: |  | Range: | e.g., 0–10 bar, 0–100 l/s |
| Calibration Date: | DD/MM/YYYY | Calibration Certificate Ref: |  |
| Output Signal: | e.g., 4-20mA | Supply Voltage: | e.g., 24V DC |
| IP Rating: | e.g., IP67 | ATEX Zone (if applicable): |  |
| Mounting Location: |  | Process Connection: | e.g., 1/2 BSP, flange DN50 |

3. Cable and Wiring Verification

| Cable Number: |  | Cable Type: | e.g., SWA, IS, screened twisted pair |
| --- | --- | --- | --- |
| Cable Route: | from — to |  |  |
| Termination — Field End: | e.g., JB-101, terminals 1-2 | Termination — Panel End: | e.g., MCC-01, terminals 5-6 |
| Cable Screen Earthed: | YES / NO — earth at one end only | Earth Point: | e.g., panel end |
| Insulation Resistance (MOhms): |  | Test Voltage: | e.g., 500V DC |
| Continuity Check (ohms): |  | Core-to-Core IR: | MOhms |

4. Loop Functional Checks

Inject / simulate signal at the field instrument and verify correct reading at the control system (PLC / SCADA / DCS). Record values at 0%, 25%, 50%, 75%, and 100% of range.

| % of Range | Process Value | Expected Signal (mA) | Measured Signal (mA) | PLC / SCADA Reading | Error (%) | Pass / Fail |
| --- | --- | --- | --- | --- | --- | --- |
| 0% |  | 4.00 |  |  |  |  |
| 25% |  | 8.00 |  |  |  |  |
| 50% |  | 12.00 |  |  |  |  |
| 75% |  | 16.00 |  |  |  |  |
| 100% |  | 20.00 |  |  |  |  |
| Downscale | < 0% | < 4.00 / 3.6 |  |  |  |  |
| Upscale | > 100% | > 20.00 / 20.5 |  |  |  |  |

5. Alarm and Trip Verification

| Alarm / Trip Description | Setpoint Value | Actual Trip Value | SCADA Annunciation OK | Output Action Verified | Pass / Fail |
| --- | --- | --- | --- | --- | --- |
| High alarm |  |  |  |  |  |
| High-high alarm / trip |  |  |  |  |  |
| Low alarm |  |  |  |  |  |
| Low-low alarm / trip |  |  |  |  |  |
| Sensor failure alarm |  |  |  |  |  |

6. Output / Final Control Element (if applicable)

| Output Device Tag: | e.g., FCV-101, pump P-201 | Type: | e.g., control valve, VSD, DOL starter |
| --- | --- | --- | --- |
| Manufacturer / Model: |  | Serial No: |  |
| Output Signal: | e.g., 4-20mA, digital DO | Fail-Safe Position: | e.g., fail closed, fail open, fail last |
| 0% Output Command: | Actual position / state | 100% Output Command: | Actual position / state |
| Stroke Time (seconds): |  | Feedback Signal Correct: | YES / NO |
| Manual Override Tested: | YES / NO / N/A | Interlock Tested: | YES / NO / N/A |

7. Additional Checks

| General Loop Checks |  |  |  |  |
| --- | --- | --- | --- | --- |
| No. | Item | Y | N | Comments |
| 1 | Instrument tag plate legible and correctly labelled in the field |  |  |  |
| 2 | Cable gland correctly fitted and sealed (IP rating maintained) |  |  |  |
| 3 | Junction box / marshalling panel wiring tidy and labelled |  |  |  |
| 4 | Instrument impulse lines / tubing free from leaks and correctly routed |  |  |  |
| 5 | Isolation valves accessible and correctly positioned (open/closed as required) |  |  |  |
| 6 | HART / digital communication verified (if applicable) |  |  |  |
| 7 | Instrument configuration parameters match data sheet (range, damping, units) |  |  |  |
| 8 | Power supply voltage at instrument within specification |  |  |  |
| 9 | No earth faults or ground loops detected |  |  |  |
| 10 | Loop response time acceptable for process requirements |  |  |  |

8. Non-Conformances / Punch List Items

| No. | Item Ref | Description | Action Required | Closed (Y/N) |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |

9. Overall Loop Check Result

| Loop Check Status | PASS / FAIL / CONDITIONAL PASS |
| --- | --- |
| Conditions (if conditional): |  |

10. Sign-Off

| Role | Name | Signature | Date |
| --- | --- | --- | --- |
| ICA Technician |  |  | DD/MM/YYYY |
| ICA Supervisor |  |  | DD/MM/YYYY |
| Commissioning Engineer |  |  | DD/MM/YYYY |
| Client Representative |  |  | DD/MM/YYYY |

11. Notes / Additional Comments

Record HART configuration screenshots, data logger references, or additional test data.

12. Document Control

| Rev | Date | Description | Author | Approved |
| --- | --- | --- | --- | --- |
| 0 |  | Initial issue |  |  |
| 1 |  |  |  |  |