Chemical Dosing Commissioning Record

MEICA Process — Chemical Dosing System Commissioning and Performance Verification

| Project and System Details |  |  |  |
| --- | --- | --- | --- |
| Document Ref: |  | Revision: |  |
| Project Name: |  | Contract No: |  |
| Site / Plant: |  | Dosing System: | e.g., ferric dosing, NaOCl dosing, polymer |
| Commissioning Date: | DD/MM/YYYY | System Tag / P&ID Ref: |  |
| Contractor: |  | Client: |  |
| Commissioning Engineer: |  | Client Witness: |  |

1. Chemical and Storage Details

| Chemical Name: | e.g., ferric sulphate, sodium hypochlorite, polyelectrolyte |  |  |
| --- | --- | --- | --- |
| Chemical Formula: |  | Concentration (%): | e.g., 12.5% w/w |
| Specific Gravity: |  | pH: |  |
| COSHH Assessment Ref: |  | Safety Data Sheet Ref: |  |
| Storage Tank Tag: |  | Tank Material: | e.g., GRP, HDPE, PP, SS 316 |
| Tank Capacity (litres): |  | Bund Capacity (%): | e.g., 110% of tank volume |
| Delivery Method: | e.g., road tanker, IBC, drum | Supplier: |  |

2. Dosing Equipment Details

| Dosing Pump Tag: |  | Duty / Standby: | e.g., duty / duty-assist / standby |
| --- | --- | --- | --- |
| Pump Type: | e.g., peristaltic, diaphragm, progressive cavity | Manufacturer / Model: |  |
| Serial Number: |  | Max Flow Rate (l/hr): |  |
| Min Flow Rate (l/hr): |  | Max Discharge Pressure (bar): |  |
| Turndown Ratio: |  | Motor Rating (kW): |  |
| Drive Type: | e.g., VSD, fixed speed, manual stroke | Control Signal: | e.g., 4-20mA, pulse, on/off |
| Dosing Line Material: | e.g., HDPE, PVC, PTFE-lined | Dosing Line Size (mm): |  |
| Injection Point Location: |  | Mixer / Flash Mixer: | e.g., in-line static mixer, mechanical |

3. Pre-Commissioning Checks

| A: Pre-Commissioning |  |  |  |  |
| --- | --- | --- | --- | --- |
| No. | Item | Y | N | Comments / Evidence |
| 1 | Mechanical installation complete — pipework, valves, fittings secure and leak-free |  |  |  |
| 2 | Pressure test of dosing pipework completed and passed |  |  |  |
| 3 | Electrical installation complete and tested (BS 7671 certificate available) |  |  |  |
| 4 | Instrument loop checks completed for all dosing-related loops |  |  |  |
| 5 | COSHH assessment reviewed and control measures in place |  |  |  |
| 6 | PPE available and correct for the chemical (gloves, goggles, face shield, chemical suit) |  |  |  |
| 7 | Emergency shower and eye wash station accessible and tested |  |  |  |
| 8 | Spill kit available at dosing area |  |  |  |
| 9 | Bund drainage valve closed and bund integrity verified |  |  |  |
| 10 | Chemical storage tank clean, inspected, and ready for filling |  |  |  |
| 11 | Tank level instrumentation calibrated and functional |  |  |  |
| 12 | Vent and overflow arrangements verified |  |  |  |
| 13 | Dosing pump primed and ready (or priming procedure available) |  |  |  |
| 14 | Non-return valves, pressure relief valves, and pulsation dampeners installed and set |  |  |  |

4. Water Commissioning (Clean Water Test)

| B: Clean Water Commissioning |  |  |  |  |
| --- | --- | --- | --- | --- |
| No. | Item | Y | N | Comments / Evidence |
| 1 | System flushed and tested with clean water before chemical introduction |  |  |  |
| 2 | Dosing pump started on clean water — no leaks, no cavitation |  |  |  |
| 3 | Pump flow rate verified at minimum, mid-range, and maximum settings |  |  |  |
| 4 | Flow rate measured using calibration vessel and stopwatch (or flow meter) |  |  |  |
| 5 | VSD / stroke adjustment operating correctly across full range |  |  |  |
| 6 | Control signal (4-20mA) driving pump output proportionally and correctly |  |  |  |
| 7 | Duty / standby changeover tested on clean water |  |  |  |
| 8 | Pressure relief valve lifting at correct set pressure |  |  |  |
| 9 | Non-return valve(s) holding correctly (no backflow) |  |  |  |
| 10 | All joints, connections, and glands leak-free under pressure |  |  |  |

5. Chemical Commissioning (Live Chemical Test)

| C: Live Chemical Commissioning |  |  |  |  |
| --- | --- | --- | --- | --- |
| No. | Item | Y | N | Comments / Evidence |
| 1 | Chemical delivered to site and stored correctly per COSHH requirements |  |  |  |
| 2 | Chemical quality verified (supplier certificate, concentration check if required) |  |  |  |
| 3 | Tank filled to correct level — level instrument reading correctly |  |  |  |
| 4 | Dosing pump started on chemical — no leaks observed |  |  |  |
| 5 | Dosing rate verified against the design dose rate (mg/l or l/hr) |  |  |  |
| 6 | Chemical reaching the injection point — verified by process measurement or visual |  |  |  |
| 7 | Residual / process measurement responding to dosing (e.g., pH, residual chlorine, turbidity) |  |  |  |
| 8 | Dosing rate adjusted to achieve target process parameter |  |  |  |
| 9 | Auto-dosing control loop tested (flow-proportional, residual-trim, or combined) |  |  |  |
| 10 | High-level and low-level tank alarms tested and annunciated on SCADA |  |  |  |
| 11 | Pump run / fault alarms tested on SCADA |  |  |  |
| 12 | Duty / standby auto-changeover on pump fault tested with chemical |  |  |  |

6. Dosing Rate Calibration

Record the pump output at various control signal settings. Measure using a calibration vessel and stopwatch.

| Control Signal (%) | Signal (mA) | Expected (l/hr) | Measured Vol. (ml) | Time (seconds) | Actual Rate (l/hr) | Error (%) |
| --- | --- | --- | --- | --- | --- | --- |
| 0 | 4 |  |  |  |  |  |
| 25 | 8 |  |  |  |  |  |
| 50 | 12 |  |  |  |  |  |
| 75 | 16 |  |  |  |  |  |
| 100 | 20 |  |  |  |  |  |

7. Safety and Environmental Checks

| D: Safety Verification |  |  |  |  |
| --- | --- | --- | --- | --- |
| No. | Item | Y | N | Comments / Evidence |
| 1 | Chemical containment bund tested (no cracks, drain closed, 110% capacity) |  |  |  |
| 2 | Emergency shower tested — adequate flow and within reach of dosing area |  |  |  |
| 3 | Eye wash station tested — clean water and within 10-second walk |  |  |  |
| 4 | Gas detection operational (chlorine detector for NaOCl systems, if applicable) |  |  |  |
| 5 | Ventilation operating in enclosed dosing rooms (LEV or general ventilation) |  |  |  |
| 6 | Warning signage in place (COSHH, chemical hazard, PPE requirements) |  |  |  |
| 7 | Spill response procedure available and operatives briefed |  |  |  |
| 8 | First aid arrangements in place for chemical exposure |  |  |  |
| 9 | Waste chemical disposal route identified and documented |  |  |  |

8. Punch List / Outstanding Items

| No. | Priority | Description | Assigned To | Cat. | Status |
| --- | --- | --- | --- | --- | --- |
| 1 | A/B/C |  |  |  | Open/Closed |
| 2 | A/B/C |  |  |  | Open/Closed |
| 3 | A/B/C |  |  |  | Open/Closed |
| 4 | A/B/C |  |  |  | Open/Closed |
| 5 | A/B/C |  |  |  | Open/Closed |
| 6 | A/B/C |  |  |  | Open/Closed |

9. Overall Commissioning Result

| Commissioning Status | PASS / CONDITIONAL PASS / FAIL |
| --- | --- |
| Conditions: |  |

10. Sign-Off

| Role | Name | Signature | Date |
| --- | --- | --- | --- |
| Commissioning Engineer |  |  | DD/MM/YYYY |
| Process Engineer |  |  | DD/MM/YYYY |
| Contractor PM |  |  | DD/MM/YYYY |
| Client Representative |  |  | DD/MM/YYYY |
| Operations Representative |  |  | DD/MM/YYYY |

11. Notes

Record calibration data, chemical certificates, photographs, or follow-up actions.

12. Document Control

| Rev | Date | Description | Author | Approved |
| --- | --- | --- | --- | --- |
| 0 |  | Initial issue |  |  |
| 1 |  |  |  |  |