Fuel Storage and Bunding Inspection Checklist

In accordance with the Control of Pollution (Oil Storage) (England) Regulations 2001 and Environment Agency guidance GPP 8

| Document Reference: | FUEL-INS- |
| --- | --- |
| Revision: | 0 |
| Inspection Date: | DD/MM/YYYY |
| Project Name: | Enter project name |
| Contract Number: | Enter contract number |
| Storage Location: | Enter location of fuel storage compound on site |
| Fuel Types Stored: | e.g., Diesel, petrol, hydraulic oil, engine oil, kerosene |
| Total Storage Volume: | litres |
| Inspector Name: | Enter name and role |

Section A: Storage Tanks, Containers, and Bunding

| No. | Storage / Bunding Check | Yes | No | N/A | Comments |
| --- | --- | --- | --- | --- | --- |
| 1 | Fuel storage tanks/bowsers are double-skinned or placed within a secondary containment bund |  |  |  |  |
| 2 | Bund capacity is at least 110% of the largest container or 25% of the total volume stored (whichever is greater) |  |  |  |  |
| 3 | Bund walls and base are impermeable with no visible cracks, gaps, or deterioration |  |  |  |  |
| 4 | Bund drain valve is closed and locked (drain valve only opened under controlled conditions to remove uncontaminated rainwater) |  |  |  |  |
| 5 | No accumulated rainwater in the bund (or water tested and confirmed uncontaminated before controlled removal) |  |  |  |  |
| 6 | Tanks and containers are in good condition with no visible leaks, corrosion, or damage |  |  |  |  |
| 7 | Tanks positioned on a firm, level base capable of supporting the full weight when loaded |  |  |  |  |
| 8 | Fill and dispensing points are within the bunded area or have drip trays fitted |  |  |  |  |
| 9 | Overfill prevention devices fitted and functioning (sight gauges, high-level alarms, automatic shut-off) |  |  |  |  |
| 10 | Tank vents unobstructed and correctly positioned |  |  |  |  |
| 11 | All tanks, containers, and pipework clearly labelled with contents and hazard information |  |  |  |  |
| 12 | Storage area located minimum 10 metres from watercourses and surface water drains |  |  |  |  |
| 13 | Storage area located away from site boundary, public areas, and buildings (minimum distances per fire risk assessment) |  |  |  |  |

Section B: Refuelling Operations

| No. | Refuelling Check | Yes | No | N/A | Comments |
| --- | --- | --- | --- | --- | --- |
| 1 | Designated refuelling area established on impermeable hardstanding with spill containment |  |  |  |  |
| 2 | Drip trays positioned under all dispensing nozzles and hose connections during refuelling |  |  |  |  |
| 3 | Nozzles fitted with automatic shut-off devices |  |  |  |  |
| 4 | Refuelling carried out by trained and authorised personnel only |  |  |  |  |
| 5 | Engines switched off during refuelling |  |  |  |  |
| 6 | No smoking signs displayed at the refuelling area and storage compound |  |  |  |  |
| 7 | Fuel dispensing records maintained (date, machine, quantity, operator) |  |  |  |  |
| 8 | Mobile bowsers fitted with drip trays, fire extinguisher, and spill kit |  |  |  |  |

Section C: Spill Response

| No. | Spill Response Check | Yes | No | N/A | Comments |
| --- | --- | --- | --- | --- | --- |
| 1 | Spill kit positioned adjacent to fuel storage area and all refuelling points |  |  |  |  |
| 2 | Spill kit contents checked weekly: absorbent pads, booms, granules, disposal bags, PPE |  |  |  |  |
| 3 | Spill response procedure displayed at the storage area |  |  |  |  |
| 4 | All personnel handling fuel trained in spill response procedure |  |  |  |  |
| 5 | Used absorbent materials disposed of as hazardous waste with consignment note |  |  |  |  |
| 6 | Environment Agency incident hotline number displayed (0800 80 70 60) |  |  |  |  |

Section D: Regulatory Compliance

| No. | Compliance Check | Yes | No | N/A | Comments |
| --- | --- | --- | --- | --- | --- |
| 1 | Oil storage compliant with the Oil Storage Regulations 2001 (England) or equivalent |  |  |  |  |
| 2 | COSHH assessment completed for all fuels and oils stored on site |  |  |  |  |
| 3 | Safety Data Sheets available for all fuels and oils |  |  |  |  |
| 4 | Fire risk assessment completed for the fuel storage area |  |  |  |  |
| 5 | Fire extinguisher(s) provided at the storage area (minimum dry powder or foam) |  |  |  |  |
| 6 | Fuel storage area secured against unauthorised access (locked compound / fencing) |  |  |  |  |
| 7 | Electrical equipment in the storage area suitable for the zone classification (if applicable) |  |  |  |  |
| 8 | Inspection records maintained and available for review |  |  |  |  |

Actions Arising

| No. | Action Required | Responsible | Priority | Target Date | Status |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |

Inspector Sign-Off

| Role | Name | Signature | Date |
| --- | --- | --- | --- |
| Inspector |  |  | DD/MM/YYYY |
| Site Manager |  |  | DD/MM/YYYY |

Document Control

| Rev. | Date | Author | Description |
| --- | --- | --- | --- |
| 0 | DD/MM/YYYY |  | Initial issue |