## Cover
EBRORA
ebrora.com
Cause-and-Effect Testing Matrix
Map every process interlock and trip against the systems it protects — record test results cause by cause, effect by effect, with pass/fail status and sign-off.
This is a free template from Ebrora. For our full range of professional-grade construction management tools, visit ebrora.com
© Ebrora 2026 — All rights reserved

## Instructions
How to Use This Template — Cause-and-Effect Testing Matrix
Step-by-Step Instructions
1. | Go to the 'C&E Matrix' sheet. Enter the Project Name, P&ID reference and Contract Number in the info strip at the top.
2. | The matrix rows list Causes — each instrument input, switch, or signal that initiates an action. Column A holds the Cause Tag (e.g. LSH-101), column B the description, and column C the set point or trigger condition.
3. | The matrix columns (from column E onwards) represent Effects — the outputs, trips, alarms, or control actions that result from each cause. Column headers show the Effect Tag and description.
4. | In each intersection cell, enter the expected response: A = Alarm, S = Shutdown / Trip, C = Control Action, or leave blank if no response is expected for that cause/effect pair.
5. | Once the test has been carried out, update the cell to show the test result: P = Pass, F = Fail, or N/T = Not Tested.
6. | The % Tested column (column D) calculates what proportion of applicable intersections have been tested for each cause row.
7. | The completion row at the bottom calculates column-by-column test completion across all causes.
8. | For any Fail result, add a note in the Notes column (far right) and raise a defect or punch list item — the interlock must be retested and passed before the SAT can be signed off.
9. | Once all cells in a row are Pass, the cause row turns green. Any row containing a Fail stays red until cleared.
10. | Print landscape for inclusion in the SAT report or the O&M commissioning records.
Colour Key
P — Pass. Cause triggered correctly and expected effect was observed.
F — Fail. Expected effect was not produced. Defect raised. Retest required.
N/T — Not Tested. Intersection identified but test not yet carried out.
A / S / C markers — Expected response defined (Alarm / Shutdown / Control). Dark navy fill.
Blank — No response expected for this cause/effect combination.
Light teal % tested column and project info — Auto-calculated.
Tips
* | Build the expected response matrix (A/S/C) from the approved Cause-and-Effect diagram on the P&IDs before testing begins. Never test against an unapproved C&E — the document must be IFC before the SAT starts.
* | Test each cause independently. Disable or bypass other causes before testing to ensure you are only observing the response to the single cause under test. Record all bypasses in the Notes column.
* | For safety-critical trips (e.g. high-high level, overpressure), the SAT must be witnessed by the Employer's Representative or an independent commissioning engineer. Record their name and signature on the test record.

## C&E Matrix
Project / Site: |  | [Enter Project / Site Name] |  |  |  | P&ID Ref: |  | [P&ID Document Reference]
Causes (Inputs / Triggers) |  |  |  | Effects (Outputs / Actions) ¦ A=Alarm S=Shutdown C=Control ¦ P=Pass F=Fail N/T=Not Tested
Cause Tag | Cause Description | Set Point / Trigger Condition | % Tested | ESD-01 | ESD-02 | XV-101 | XV-201 | ALM-HH | ALM-H | ALM-L | ALM-LL | BLW-01 | BLW-02 | SCADA | PAGE | Notes / Defect Ref
|  |  |  | Emergency Shutdown Pump PST-01 | Emergency Shutdown Pump PST-02 | Close Inlet Isolation Valve XV-101 | Close Outlet Valve XV-201 | Activate HH Level Alarm | Activate H Level Alarm | Activate L Level Alarm | Activate LL Level Alarm | Trip Blower 01 | Trip Blower 02 | SCADA Fault Annunciation | Operator Pager / Alarm
LSH-101 | Level Switch High-High — Inlet Chamber | Set: 2850mm / Normal WL 2200mm | 100% | P | P | P |  | P | [5 empty] | P | P
LSH-102 | Level Switch High — Inlet Chamber | Set: 2600mm / Normal WL 2200mm | 100% | [5 empty] | P |  |  |  |  | P | P
LSL-101 | Level Switch Low — Inlet Chamber | Set: 800mm / Normal WL 2200mm | 100% | [6 empty] | P |  |  |  | P
LSL-102 | Level Switch Low-Low — Inlet Chamber | Set: 400mm / Normal WL 2200mm | 100% | P | P | [5 empty] | P |  |  | P | F | ESD pager (effect col 11) — FAIL. Pager relay wired to wrong output. Defect DF-019 raised.
PSH-201 | Pressure Switch High — Inlet Rising Main DN300 | Set: 8.5 bar g (WP 7.0 bar g) | 50% | P |  | P | [7 empty] | N/T | N/T | PSH-201 — SCADA/pager not yet tested. Commissioning team returning 25/03.
PSL-201 | Pressure Switch Low — Inlet Rising Main DN300 | Set: 0.5 bar g (no-flow detect) | 0% | [10 empty] | A | A
TSH-301 | Temperature Switch High — MCC-01 Panel | Set: 45°C | 0% | [10 empty] | A | A
FSL-401 | Flow Switch Low — Aeration Air Supply | Set: 85 m³/h (min design flow) | 0% | [8 empty] | S | S | A | A
XS-MCC01 | MCB Trip / Fault Signal — MCC-01 | Fault output from MCC-01 relay | 0% | [10 empty] | A | A
ESD-PB | Emergency Stop Pushbutton — Local Panel | Hardwired E-Stop at pump station | 0% | S | S | S | S |  |  |  |  | S | S | A | A
GD-001 | Gas Detector High — H₂S Monitor, Inlet Chamber | Set: 5 ppm (LEL 10% not applicable) | 0% | S | S | S | [7 empty] | A | A
VS-BLW01 | Vibration Switch High — Blower 01 | Set: 15 mm/s RMS | 0% | [8 empty] | S |  | A | A
COLUMN TEST COMPLETION % |  |  |  | 60% | 50% | 50% | 0% | 100% | 100% | 100% | 100% | 0% | 0% | 33.33% | 27.27%

## Terms of Use (hidden)
EBRORA — TERMS OF USE
This template is provided free of charge by Ebrora (ebrora.com) for personal and professional use.
LICENCE: You may use this template for your own projects. You may not resell, redistribute, or claim authorship of this template.
NO WARRANTY: This template is provided "as is" without warranty of any kind. Ebrora accepts no liability for errors, omissions, or losses arising from use of this template.
INTELLECTUAL PROPERTY: All design, layout, branding, and content remain the intellectual property of Ebrora.
MODIFICATIONS: You may modify this template for your own use. Modified versions may not be distributed or sold.
ATTRIBUTION: If you share outputs generated using this template, attribution to Ebrora (ebrora.com) is appreciated but not required.
SUPPORT: For queries, feedback, or to report errors, contact support@ebrora.com.
For our full range of professional construction management tools, visit ebrora.com.