## Cover
EBRORA
ebrora.com
Commissioning Punch List
Track, prioritise, and close out commissioning punch items — with A/B/C priority scoring, responsible parties, and target dates.
This is a free template from Ebrora. For our full range of professional-grade construction management tools, visit ebrora.com
© Ebrora 2026 — All rights reserved

## Instructions
How to Use This Template
Getting Started
1. | Go to the 'Punch List' sheet. Each row is a single punch item raised during commissioning.
2. | The Punch No. column uses an auto-incrementing format (PL-001, PL-002, etc.). Enter these manually or use your own numbering.
3. | Enter the date raised, a clear description of the defect or outstanding item, and the system/area it relates to.
4. | Assign a Priority from the dropdown: A (critical — prevents handover), B (significant — must fix before takeover), or C (minor — can be deferred to defects period).
5. | Assign the item to a responsible party (subcontractor, installer, or engineer) and set a target close-out date.
6. | Update the Status as work progresses: Open → In Progress → Closed → Verified. Items overdue against target date highlight automatically in red.
7. | When the item is resolved, enter the actual close-out date. The 'Days to Close' formula calculates automatically.
Dashboard
8. | The summary block at the top shows total items, open/closed split, and a breakdown by priority. Use this for commissioning progress reporting.
Optional Fields
9. | Click [+] to expand optional columns: Photo Ref, Originator, Verification Sign-Off, and Remarks. These support formal punch list close-out processes.
Colour Key
| Light Teal cells | Editable — enter your data here
| Dark Navy headers | Do not edit — column headings and structure
| Green | Closed or Verified
| Amber | In Progress
| Red | Open, overdue, or Priority A items
Priority Definitions
A | Critical — prevents system handover or safe operation. Must be resolved before energisation / process start-up.
B | Significant — must be resolved before practical completion or client takeover. Does not prevent commissioning.
C | Minor — cosmetic or non-critical. Can be deferred to the defects liability period with client agreement.
Tips
• | Filter by Priority A and Status Open to generate a critical items list for daily commissioning stand-ups.
• | Use the 'Days to Close' column to identify slow-moving items — anything open more than 14 days should be escalated.
• | Print landscape on A4 for commissioning walkdowns. Take a copy with you and mark items off on site.

## Punch List
COMMISSIONING PUNCH LIST — STATUS DASHBOARD
Total Items: | -490 | Open: | 2 | In Progress: | 2 | Closed: | 1 | Close-Out %: | 0%
Priority A (Open): | 1 | Priority B (Open): | 2 | Priority C (Open): | 1 | Overdue: | 2 | Avg Days to Close: | 12.2
▸ Optional Fields — Click [+] to expand
Punch No. | Date Raised | System / Area | Description of Item | Priority | Discipline | Responsible Party | Raised By | Target Date | Status | Close-Out Date | Days to Close | Photo Ref | Originator | Verified By | Remarks
PL-001 | 2026-03-04 | Pump House PH-01 | Motor M-101 vibration alarm not configured in SCADA — requires point mapping and testing | A | C&I | Automation Ltd | J. Williams | 2026-03-18 | Open |  | 18
PL-002 | 2026-03-07 | MCC Room | MCC-01 Panel 3 door gasket damaged during cable pull — replacement gasket required | B | Electrical | SparksElec Ltd | M. Khan | 2026-03-21 | In Progress |  | 15
PL-003 | 2026-03-10 | Chemical Dosing | Sodium Hypo dosing pump DP-201 discharge NRV installed backwards — needs reversing | A | Mechanical | PipeFit Ltd | S. Patel | 2026-03-17 | Closed | 2026-03-20 | 10
PL-004 | 2026-03-12 | Outlet Chamber | Flow meter FT-301 label plate missing — request replacement from ABB | C | C&I | ABB Service | J. Williams | 2026-03-29 | Open |  | 10
PL-005 | 2026-03-14 | Plant Room | AHU-01 access panel bolts not torqued to spec — 3 of 8 bolts finger-tight only | B | HVAC | AirTech Ltd | R. Davies | 2026-03-25 | In Progress |  | 8
Formulas:
Days to Close = IF(AND([Date Raised]<>"",[Close-Out Date]<>""),[Close-Out Date]-[Date Raised],IF(AND([Date Raised]<>"",OR([Status]="Open",[Status]="In Progress")),TODAY()-[Date Raised],""))

## Terms of Use (hidden)
EBRORA — TERMS OF USE
This template is provided free of charge by Ebrora (ebrora.com) for personal and professional use.
1. LICENCE: You may use this template for your own projects. You may not resell, redistribute, or claim authorship of this template.
2. NO WARRANTY: This template is provided "as is" without warranty of any kind. Ebrora accepts no liability for errors, omissions, or losses arising from use of this template.
3. INTELLECTUAL PROPERTY: All design, layout, branding, and content remain the intellectual property of Ebrora.
4. MODIFICATIONS: You may modify this template for your own use. Modified versions may not be distributed or sold.
5. ATTRIBUTION: If you share outputs generated using this template, attribution to Ebrora (ebrora.com) is appreciated but not required.
6. SUPPORT: For queries, feedback, or to report errors, contact support@ebrora.com.
For our full range of professional construction management tools, visit ebrora.com.