## Cover
EBRORA
ebrora.com
Control Philosophy Compliance Checklist
Systematically verify that installed control systems comply with the approved control philosophy — covering modes of operation, interlocks, alarms, sequencing, and safety functions with scored compliance tracking.
This is a free template from Ebrora. For our full range of professional-grade construction management tools, visit ebrora.com
© Ebrora 2026 — All rights reserved

## Instructions
How to Use This Template
1. Open the 'Compliance Checklist' sheet. Start by filling in the form header with the system under review, the control philosophy document reference, and the review team details.
2. The checklist is organised into five control function categories, each with a teal band: Modes of Operation, Interlocks & Trips, Alarm Management, Sequencing & Logic, and Safety / SIL Functions.
3. Each row contains a specific control philosophy requirement. The 'CP Reference' column shows the clause or section number from the control philosophy document.
4. For each requirement, record the Compliance Status using the dropdown: Compliant, Non-Compliant, Deviation Accepted, or N/A.
5. Each category band auto-calculates its compliance score — the percentage of applicable items marked Compliant or Deviation Accepted.
6. The Compliance Dashboard on the right shows scores per category with a visual bar and an overall compliance verdict (Compliant / Non-Compliant).
7. For any Non-Compliant items, record the deviation description and the agreed corrective action in the core columns.
8. Expand the optional columns for verification method, evidence reference, review date, and reviewer sign-off.
Colour Key
Light teal cells = user input / editable fields
Dark navy headers = do not edit
Teal bands = category section headers (do not edit)
Green = Compliant or Deviation Accepted
Amber = Partial compliance (category 80–99%)
Red = Non-Compliant or category below 80%
Tips
• Work through this checklist with the control philosophy document open side-by-side — the CP Reference column links each check to the exact clause.
• A 'Deviation Accepted' status must always have a documented justification — don't use it to paper over genuine non-compliance.
• Complete this checklist before the Functional Performance Test (FPT). Any non-compliant items should be resolved before the system goes live.

## Compliance Checklist
Control Philosophy Compliance Checklist | [6 empty] | Compliance Dashboard
System / Asset: | Raw Water Pumping System |  | Project: | Millbrook WTW |  |  | Category | Compliance | Score | Visual
System Tag: | SYS-RWP-01 |  | Location: | Pumphouse A |  |  | Modes of Operation | 83.33% | ⚠️ | █████████████
Control Philosophy Doc Ref: | CP-RWP-01 Rev C |  | PLC / Controller Ref: | PLC-CAB-01 (Siemens S7-1500) |  |  | Interlocks & Trips | 85.71% | ⚠️ | █████████████
CP Revision: | Rev C (issued 15/01/2026) |  | SCADA System: | WinCC OA v3.19 |  |  | Alarm Management | 100% | ✅ | ███████████████
Review Lead: | M. Clarke — ACE Commissioning |  | Contractor: | Integrated Automation Ltd |  |  | Sequencing & Logic | 85.71% | ⚠️ | █████████████
Review Date: | 2026-03-20 |  | Client Witness: | J. Patel (Client) |  |  | Safety / SIL Functions | 100% | ✅ | ███████████████
[7 empty] | OVERALL COMPLIANCE | 90.62% | NON-COMPLIANT
Ref | CP Clause | Control Philosophy Requirement | Compliance | Priority | Deviation / Observation | Corrective Action | Verification Method | Evidence / Doc Ref | Review Date | Reviewed By
▼ Modes of Operation |  |  | Compliance: 83%
1 | CP-1.1 | Auto/Manual mode selection available at local panel and SCADA | Compliant | Critical
2 | CP-1.2 | Hand mode overrides auto mode and is indicated on SCADA | Compliant | Critical
3 | CP-1.3 | Mode transitions are bumpless (no process upset on changeover) | Compliant | High
4 | CP-1.4 | Remote/Local selector switch functional and indicated | Compliant | Medium
5 | CP-1.5 | Duty/Standby/Assist selection logic matches CP specification | Compliant | Critical
6 | CP-1.6 | Lead pump auto-rotation operates per defined schedule | Non-Compliant | High | Rotation logic not implemented — all pumps fixed to manual lead selection | Software update required. IAL to implement rotation logic by 28/03/2026
▼ Interlocks & Trips |  |  | Compliance: 86%
7 | CP-2.1 | High-high level trip stops all pumps within specified time | Compliant | Critical
8 | CP-2.2 | Low-low level trip prevents pump dry running | Compliant | Critical
9 | CP-2.3 | Motor overload trip operates and is indicated on SCADA | Compliant | Critical
10 | CP-2.4 | Vibration high trip stops affected pump and raises alarm | Non-Compliant | High | Vibration sensor on Pump 3 not connected — cable route incomplete | Briggs to complete cable pull and terminate by 25/03/2026
11 | CP-2.5 | Bearing temperature high trip operates at set point | Compliant | High
12 | CP-2.6 | Interlock reset requires manual acknowledgement | Compliant | Medium
13 | CP-2.7 | All trip conditions are logged with timestamp in SCADA historian | Compliant | High
▼ Alarm Management |  |  | Compliance: 100%
14 | CP-3.1 | Alarm set points match those specified in control philosophy | Compliant | Critical
15 | CP-3.2 | Alarm priorities assigned per CP (Critical / High / Medium / Low) | Deviation Accepted | Medium | Alarm priorities simplified to 3 tiers instead of 4 — agreed with client | Documented in deviation register DR-017. No corrective action required.
16 | CP-3.3 | Alarm acknowledgement requires operator action | Compliant | Medium
17 | CP-3.4 | Alarm history retained for minimum 12 months | Compliant | Low
18 | CP-3.5 | Nuisance alarm suppression logic implemented per CP | Compliant | Medium
19 | CP-3.6 | First-out alarm indication functional for trip sequences | Compliant | High
▼ Sequencing & Logic |  |  | Compliance: 86%
20 | CP-4.1 | Start sequence follows CP step order exactly | Compliant | Critical
21 | CP-4.2 | Stop sequence follows CP step order with correct time delays | Compliant | Critical
22 | CP-4.3 | Auto changeover on lead pump failure within specified time | Compliant | Critical
23 | CP-4.4 | PID control loops tuned to achieve CP performance targets | Non-Compliant | High | PID loop for flow control oscillating — tuning parameters not optimised | ACE to retune PID loop during wet commissioning. Target: stable within ±2%
24 | CP-4.5 | Flow pacing / modulating control responds correctly to demand | Compliant | High
25 | CP-4.6 | Timer values match CP specification (start delays, run-on times) | Compliant | Medium
26 | CP-4.7 | Sequential interlocks prevent out-of-sequence operation | Compliant | High
▼ Safety / SIL Functions |  |  | Compliance: 100%
27 | CP-5.1 | Emergency stop (E-Stop) de-energises all drives immediately | Compliant | Critical
28 | CP-5.2 | E-Stop requires manual reset and physical key release | Compliant | Critical
29 | CP-5.3 | SIL-rated functions operate independently of PLC | Compliant | Critical
30 | CP-5.4 | Safety relay / SIL controller wiring matches safety circuit drawings | Compliant | Critical
31 | CP-5.5 | Proof test intervals documented and scheduled | Compliant | High
32 | CP-5.6 | Safety function test records match SIL verification report | Compliant | High

## Terms of Use (hidden)
EBRORA — TERMS OF USE
This template is provided free of charge by Ebrora (ebrora.com) for personal and professional use.
1. LICENCE: You may use this template for your own projects. You may not resell, redistribute, or claim authorship of this template.
2. NO WARRANTY: This template is provided "as is" without warranty of any kind. Ebrora accepts no liability for errors, omissions, or losses arising from use of this template.
3. INTELLECTUAL PROPERTY: All design, layout, branding, and content remain the intellectual property of Ebrora.
4. MODIFICATIONS: You may modify this template for your own use. Modified versions may not be distributed or sold.
5. ATTRIBUTION: If you share outputs generated using this template, attribution to Ebrora (ebrora.com) is appreciated but not required.
6. SUPPORT: For queries, feedback, or to report errors, contact support@ebrora.com.
For our full range of professional construction management tools, visit ebrora.com.