## Cover
EBRORA
ebrora.com
Functional Performance Test Log
Document and track functional performance testing of mechanical and electrical systems — recording test parameters, acceptance criteria, measured results, and pass/fail outcomes with automatic scoring.
This is a free template from Ebrora. For our full range of professional-grade construction management tools, visit ebrora.com
© Ebrora 2026 — All rights reserved

## Instructions
How to Use This Template
1. Open the 'FPT Log' sheet. The top section is a form-style header where you enter the project details, system under test, and test team information. Fill this in once per test session.
2. The main test log starts below the header. Each row represents one test parameter or check point within the functional performance test.
3. Enter the Test Ref (sequential numbering), the test description, and the acceptance criteria — this is the benchmark the system must meet to pass.
4. Record the measured/observed value in the 'Actual Result' column and select the Result (Pass/Fail/N/A) from the dropdown.
5. The Score Summary panel on the right auto-calculates: total tests, pass count, fail count, and overall pass rate. These update in real time as you fill in results.
6. Use the Severity column for any failures — Critical, Major, or Minor. This helps prioritise remedial actions.
7. Expand the optional columns for witness details, re-test dates, and sign-off fields for formal commissioning records.
8. Once all tests are complete, fill in the Overall Outcome and Signatures section at the bottom of the form header for formal sign-off.
Colour Key
Light teal cells = user input / editable fields
Dark navy headers = do not edit
Green = Pass (test met acceptance criteria)
Red = Fail (test did not meet criteria)
Amber = Re-test required or conditional pass
Tips
• Write acceptance criteria precisely — 'Flow rate ≥ 45 l/s at 2.5 bar' is better than 'Flow adequate'. Measurable criteria prevent disputes.
• Record actual values even for passing tests — this creates a baseline for future performance comparisons and O&M handover.
• For complex systems, create one copy of this template per system or sub-system. Name each file clearly (e.g., FPT-HVAC-AHU01).

## FPT Log
Functional Performance Test Log | [8 empty] | Score Summary
Project Name: | Millbrook Water Treatment Works |  | Location / Building: | Pumphouse A |  |  |  |  | Total Tests |  | 7
System / Equipment: | Raw Water Pumping System |  | Contractor: | Briggs Electrical Ltd |  |  |  |  | Tests Passed |  | 5
System Tag / Ref: | SYS-RWP-01 |  | Specification Ref: | Spec Section 8.3.2 |  |  |  |  | Tests Failed |  | 2
Test Procedure Ref: | FPT-PROC-012 Rev B |  | Weather / Conditions: | Dry, 12°C, low wind |  |  |  |  | Tests N/A |  | 0
Test Date: | 2026-03-15 |  | Client Rep: | J. Patel |  |  |  |  | Pass Rate |  | 71.43%
Test Engineer: | M. Clarke — ACE Commissioning |  | Commissioning Manager: | M. Clarke |  |  |  |  | Critical Failures |  | 0
Witness(es): | J. Patel (Client), R. Evans (D&B Contractor) |  | Pre-Req Checks Complete: | Yes |  |  |  |  | Overall Outcome
Test Parameters & Results | [8 empty] | ▸ Optional Fields — Click [+] to expand
Test Ref | Test Category | Test Description / Parameter | Acceptance Criteria | Actual Result / Measured Value | Result | Severity | Responsible | Remarks / Action Required | Witness Name | Witness Sign-Off | Re-Test Date | Re-Test Result
FPT-001 | Pre-Start Checks | All isolation valves open and tagged | Valves FV-101, FV-102, FV-103 confirmed open | All 3 valves confirmed open and tagged | Pass | N/A | M. Clarke
FPT-002 | Electrical | Motor insulation resistance ≥ 2 MΩ | IR ≥ 2 MΩ at 500V DC | 3.8 MΩ (Pump 1), 4.1 MΩ (Pump 2), 3.5 MΩ (Pump 3) | Pass | N/A | R. Evans
FPT-003 | Mechanical | Pump 1 flow rate at duty point | Flow ≥ 45 l/s at 2.5 bar TDH | 47.2 l/s at 2.48 bar | Pass | N/A | M. Clarke
FPT-004 | Performance | Pump 2 flow rate at duty point | Flow ≥ 45 l/s at 2.5 bar TDH | 38.6 l/s at 2.52 bar | Fail | Major | M. Clarke | Below duty — impeller check required. Punch item #P-051 raised.
FPT-005 | Control / SCADA | Auto changeover on lead pump trip | Standby pump starts within 15 seconds of lead pump trip | Standby started in 8.3 seconds | Pass | N/A | M. Clarke
FPT-006 | Safety | High-high level alarm triggers pump stop | Pumps stop within 5 seconds of HH level | Pumps stopped in 3.1 seconds | Pass | N/A | J. Patel
FPT-007 | Environmental | Noise level at site boundary | Noise ≤ 55 dB(A) at nearest receptor | 58.2 dB(A) measured | Fail | Minor | R. Evans | Marginal exceedance — acoustic enclosure adjustment needed

## Terms of Use (hidden)
EBRORA — TERMS OF USE
This template is provided free of charge by Ebrora (ebrora.com) for personal and professional use.
1. LICENCE: You may use this template for your own projects. You may not resell, redistribute, or claim authorship of this template.
2. NO WARRANTY: This template is provided "as is" without warranty of any kind. Ebrora accepts no liability for errors, omissions, or losses arising from use of this template.
3. INTELLECTUAL PROPERTY: All design, layout, branding, and content remain the intellectual property of Ebrora.
4. MODIFICATIONS: You may modify this template for your own use. Modified versions may not be distributed or sold.
5. ATTRIBUTION: If you share outputs generated using this template, attribution to Ebrora (ebrora.com) is appreciated but not required.
6. SUPPORT: For queries, feedback, or to report errors, contact support@ebrora.com.
For our full range of professional construction management tools, visit ebrora.com.