## Cover
EBRORA
ebrora.com
Pre-Commissioning Checklist
A structured, category-banded checklist to verify that all mechanical, electrical, instrumentation, civil, and documentation prerequisites are complete before commissioning begins.
This is a free template from Ebrora. For our full range of professional-grade construction management tools, visit ebrora.com
© Ebrora 2026 — All rights reserved

## Instructions
How to Use This Template
1. Open the 'Pre-Comm Checklist' sheet. The top section contains form fields for the system/asset being checked — fill these in first.
2. The checklist is organised into five discipline categories, each with a teal category band: Mechanical, Electrical, Instrumentation, Civil / Structural, and Documentation.
3. Work through each check item row by row. Select Pass, Fail, or N/A from the Result dropdown in column D.
4. Each category band has an auto-calculated completion score showing the percentage of items passed within that discipline.
5. The Readiness Dashboard on the right side updates in real time — showing pass rates per category and an overall commissioning readiness score.
6. For any item marked Fail, add a note in the Remarks column and assign a responsible person to resolve it before commissioning.
7. Expand the optional columns for sign-off details: date checked, checked by, and evidence/reference document number.
8. The system is only ready for commissioning when Overall Readiness reaches 100% (all applicable items passed). The dashboard will show green when ready.
Colour Key
Light teal cells = user input / editable fields
Dark navy headers = do not edit
Teal category bands = discipline section headers (do not edit)
Green = Pass / Ready / 100% complete
Amber = Partially complete (50–99%)
Red = Fail / Not ready / Below 50%
Tips
• Complete this checklist before calling the commissioning team to site — failed pre-commissioning items are the number one cause of wasted commissioning days.
• Use N/A for items that genuinely don't apply to this system. Don't leave items blank — blank items won't count toward the readiness score.
• Keep a copy of the completed checklist in the commissioning file for each system — it's a key handover document.

## Pre-Comm Checklist
Pre-Commissioning Checklist | [5 empty] | Readiness Dashboard
Project: | Millbrook Water Treatment Works |  | Date: | 2026-03-18 |  | Category | Pass Rate | Visual
System / Asset: | Raw Water Pumping System |  | Specification Ref: | Spec 8.3 |  | Mechanical | 87.5% | █████████████
System Tag: | SYS-RWP-01 |  | Drawing Ref: | DWG-M-101 Rev C |  | Electrical | 100% | ███████████████
Location: | Pumphouse A |  | Commissioning Manager: | M. Clarke |  | Instrumentation | 83.33% | █████████████
Contractor: | Briggs Electrical Ltd / ACE Controls |  | Client Representative: | J. Patel |  | Civil / Structural | 80% | ████████████
Checklist Prepared By: | M. Clarke |  | Checklist Date: | 2026-03-18 |  | Documentation | 100% | ███████████████
[6 empty] | OVERALL READINESS | 90.32% | ❌ NOT READY
Ref | Category | Check Item | Result | Responsible | Remarks / Action | Date Checked | Checked By | Evidence / Doc Ref
▼ Mechanical |  |  | Completion: 88%
M-01 | Mechanical | All pipework installed, supported, and pressure tested | Pass | Briggs
M-02 | Mechanical | Valves installed, correct orientation confirmed, and operable | Pass | Briggs
M-03 | Mechanical | Pump / motor alignment checked and recorded | Pass | ACE
M-04 | Mechanical | Coupling guards and safety covers fitted | Pass | Briggs
M-05 | Mechanical | Lubrication completed per manufacturer's schedule | Pass | ACE
M-06 | Mechanical | Vibration isolators / anti-vibration mounts installed | Pass | Briggs
M-07 | Mechanical | Direction of rotation confirmed (bump test) | Pass | ACE | CW rotation confirmed
M-08 | Mechanical | Gland packing / mechanical seals checked | Fail | Briggs | Pump 2 gland leaking — replacement ordered
▼ Electrical |  |  | Completion: 100%
E-01 | Electrical | Power supply cables installed, terminated, and meggered | Pass | Briggs
E-02 | Electrical | Earth bonding complete and tested (≤ 1Ω) | Pass | Briggs | 0.3Ω measured
E-03 | Electrical | Motor insulation resistance tested (≥ 2 MΩ) | Pass | Briggs | 3.8/4.1/3.5 MΩ
E-04 | Electrical | Overload / protection settings confirmed per design | Pass | Briggs
E-05 | Electrical | Isolation and lock-off facilities functional | Pass | Briggs
E-06 | Electrical | Local control panel energised and functional | Pass | Briggs
E-07 | Electrical | Emergency stop circuits tested and proven | Pass | Briggs
▼ Instrumentation |  |  | Completion: 83%
I-01 | Instrumentation | All instruments installed per P&ID | Pass | ACE
I-02 | Instrumentation | Instrument loop checks completed (see Loop Check Register) | Pass | ACE | See Loop Check Register
I-03 | Instrumentation | Transmitters calibrated within specified tolerance | Fail | ACE | LT-205 out of tolerance — recalibration scheduled
I-04 | Instrumentation | Control valves stroked and confirmed full travel | Pass | ACE
I-05 | Instrumentation | SCADA / PLC points verified against I/O schedule | Pass | ACE
I-06 | Instrumentation | Alarm set points configured per control philosophy | Pass | ACE
▼ Civil / Structural |  |  | Completion: 80%
CS-01 | Civil / Structural | Foundations / plinths complete and cured | Pass | Main Contractor
CS-02 | Civil / Structural | Equipment bolted down and torque values recorded | Pass | Main Contractor
CS-03 | Civil / Structural | Drainage and bunding adequate for spill containment | Pass | Main Contractor
CS-04 | Civil / Structural | Access platforms, ladders, and handrails installed | Pass | Main Contractor
CS-05 | Civil / Structural | Floor / area clean and free of construction debris | Fail | Main Contractor | Debris in pump well — clean-up required before wet comm
▼ Documentation |  |  | Completion: 100%
D-01 | Documentation | O&M manuals received and filed | Pass | ACE
D-02 | Documentation | As-built drawings available and up to date | Pass | ACE
D-03 | Documentation | Test certificates received (FAT, pressure, electrical) | Pass | ACE
D-04 | Documentation | RAMS / method statements approved for commissioning | Pass | ACE
D-05 | Documentation | Permit to work arrangements in place | Pass | M. Clarke
D-06 | Documentation | Commissioning procedure reviewed and approved | N/A |  | Procedure under final review

## Terms of Use (hidden)
EBRORA — TERMS OF USE
This template is provided free of charge by Ebrora (ebrora.com) for personal and professional use.
1. LICENCE: You may use this template for your own projects. You may not resell, redistribute, or claim authorship of this template.
2. NO WARRANTY: This template is provided "as is" without warranty of any kind. Ebrora accepts no liability for errors, omissions, or losses arising from use of this template.
3. INTELLECTUAL PROPERTY: All design, layout, branding, and content remain the intellectual property of Ebrora.
4. MODIFICATIONS: You may modify this template for your own use. Modified versions may not be distributed or sold.
5. ATTRIBUTION: If you share outputs generated using this template, attribution to Ebrora (ebrora.com) is appreciated but not required.
6. SUPPORT: For queries, feedback, or to report errors, contact support@ebrora.com.
For our full range of professional construction management tools, visit ebrora.com.