## Cover
EBRORA
ebrora.com
Process Proving
KPI Tracker
Track sample results against consent limits during process proving
with automated pass/fail assessment and compliance KPIs.
This is a free template from Ebrora.
For our full range of professional-grade construction management tools, visit ebrora.com
© Ebrora 2026 — All rights reserved

## Instructions
How to Use This Template
Getting Started
1. | This template has two working sheets: the 'Dashboard' (summary KPIs) and the 'Sample Data' (detailed results log).
2. | Start with the 'Sample Data' sheet. Each row records one sample result for one parameter.
3. | Enter the Sample Ref, Date, Parameter (from dropdown), Consent Limit, Limit Type, and actual Result.
4. | The Pass/Fail column auto-calculates based on the Result vs Consent Limit. For 'Max' limits, Result must be ≤ Limit to pass.
5. | The 'Dashboard' sheet auto-updates with KPIs: total samples, pass rate, failures by parameter, and consent compliance.
6. | Parameters include: BOD, Suspended Solids, Ammonia, Total Phosphorus, pH (lower), pH (upper), Flow, and Total Nitrogen.
7. | All formulas reference the Sample Data sheet — do not manually edit the Dashboard KPI values.
Colour Key
Light teal cells (#E8F6F7) = User input / editable fields
Dark navy headers (#1B2A4A) = Do not edit
Green = Pass (result within consent limit)
Red = Fail (result exceeds consent limit)
Amber = Approaching limit (result ≥ 80% of consent limit)
Tips
Tip 1: | During process proving, sample daily and log results immediately. Gaps in the data record will be flagged by the EA/regulator.
Tip 2: | Use the Dashboard to present compliance evidence at progress meetings — it's far more effective than a spreadsheet of raw numbers.
Tip 3: | If a parameter fails, record the corrective action in the Notes column. This demonstrates proactive management to the regulator.

## Dashboard
Process Proving — Compliance Dashboard
Total Samples |  | Overall Pass Rate |  | Total Failures |  | Parameters Tracked
15 |  | 86.67% |  | 2 |  | 8
Compliance by Parameter
Parameter | Samples | Passes | Fails | Pass Rate | Avg Result | Consent Limit | Status
BOD | 3 | 2 | 1 | 66.67% | 16.7667 | 20 | Non-Compliant
Suspended Solids | 3 | 2 | 1 | 66.67% | 26 | 30 | Non-Compliant
Ammonia | 3 | 3 | 0 | 100% | 3.3667 | 5 | Compliant
Total Phosphorus | 2 | 2 | 0 | 100% | 0.735 | 1 | Compliant
pH (lower) | 1 | 1 | 0 | 100% | 7.1 | 6 | Compliant
pH (upper) | 1 | 1 | 0 | 100% | 7.8 | 9 | Compliant
Flow | 1 | 1 | 0 | 100% | 4200 | 5000 | Compliant
Total Nitrogen | 1 | 1 | 0 | 100% | 11.5 | 15 | Compliant

## Sample Data
Sample Ref | Date | Parameter | Consent Limit | Limit Type | Unit | Result | Pass / Fail | Sampled By | Lab Ref | Notes
PP-001 | 2026-03-10 | BOD | 20 | Max | mg/l | 12.5 | Pass | A. Khan | LAB-2026-0441
PP-002 | 2026-03-10 | Suspended Solids | 30 | Max | mg/l | 18 | Pass | A. Khan | LAB-2026-0442
PP-003 | 2026-03-10 | Ammonia | 5 | Max | mg/l | 3.2 | Pass | A. Khan | LAB-2026-0443
PP-004 | 2026-03-10 | Total Phosphorus | 1 | Max | mg/l | 0.85 | Pass | A. Khan | LAB-2026-0444 | Approaching limit
PP-005 | 2026-03-10 | pH (lower) | 6 | Min | pH | 7.1 | Pass | A. Khan | LAB-2026-0445
PP-006 | 2026-03-17 | BOD | 20 | Max | mg/l | 15.8 | Pass | J. Davies | LAB-2026-0501
PP-007 | 2026-03-17 | Suspended Solids | 30 | Max | mg/l | 35 | Fail | J. Davies | LAB-2026-0502 | Failed — increased RAS rate
PP-008 | 2026-03-17 | Ammonia | 5 | Max | mg/l | 4.8 | Pass | J. Davies | LAB-2026-0503 | Close to limit
PP-009 | 2026-03-17 | Total Phosphorus | 1 | Max | mg/l | 0.62 | Pass | J. Davies | LAB-2026-0504
PP-010 | 2026-03-17 | pH (upper) | 9 | Max | pH | 7.8 | Pass | J. Davies | LAB-2026-0505
PP-011 | 2026-03-21 | BOD | 20 | Max | mg/l | 22 | Fail | A. Khan | LAB-2026-0561 | Failed — storm event, notified EA
PP-012 | 2026-03-21 | Suspended Solids | 30 | Max | mg/l | 25 | Pass | A. Khan | LAB-2026-0562
PP-013 | 2026-03-21 | Ammonia | 5 | Max | mg/l | 2.1 | Pass | A. Khan | LAB-2026-0563
PP-014 | 2026-03-21 | Flow | 5000 | Max | m³/d | 4200 | Pass | A. Khan | LAB-2026-0564 | DWF measurement
PP-015 | 2026-03-21 | Total Nitrogen | 15 | Max | mg/l | 11.5 | Pass | A. Khan | LAB-2026-0565

## Terms of Use (hidden)
EBRORA — TERMS OF USE
This template is provided free of charge by Ebrora (ebrora.com) for personal and professional use.
LICENCE: You may use this template for your own projects. You may not resell, redistribute, or claim authorship of this template.
NO WARRANTY: This template is provided "as is" without warranty of any kind. Ebrora accepts no liability for errors, omissions, or losses arising from use of this template.
INTELLECTUAL PROPERTY: All design, layout, branding, and content remain the intellectual property of Ebrora.
MODIFICATIONS: You may modify this template for your own use. Modified versions may not be distributed or sold.
ATTRIBUTION: If you share outputs generated using this template, attribution to Ebrora (ebrora.com) is appreciated but not required.
SUPPORT: For queries, feedback, or to report errors, contact support@ebrora.com.
For our full range of professional construction management tools, visit ebrora.com.