## Cover
EBRORA
ebrora.com
Loop Check Register
Record and track instrument loop checks with scored pass/fail criteria — wiring verification, signal simulation, calibration, and functional testing — with automatic completion scoring.
This is a free template from Ebrora. For our full range of professional-grade construction management tools, visit ebrora.com
© Ebrora 2026 — All rights reserved

## Instructions
How to Use This Template
1. Open the 'Loop Check Register' sheet. Each row represents one instrument loop on your project.
2. Enter the Loop Tag (e.g., FIT-101, LT-205) and the associated instrument description, P&ID reference, and system/area.
3. For each loop, score the four check categories using the dropdowns: Wiring Check, Signal Simulation, Calibration Check, and Functional Test. Options are Pass, Fail, or N/A.
4. The Score column auto-calculates the percentage of checks passed (N/A items are excluded from the count). The Overall Status updates automatically based on the score.
5. Record the date checked and the name of the person who performed the loop check in the core columns.
6. Expand the optional columns for additional detail: expected signal range, actual reading, test equipment reference, and punch list items.
7. Use the Summary Dashboard at the top to monitor overall progress — total loops, pass rates, and status breakdown update in real time.
8. Filter by system/area or status to create focused commissioning reports for specific zones or disciplines.
Colour Key
Light teal cells = user input / editable fields
Dark navy headers = do not edit
Green = All checks passed (100% score)
Amber = Partially complete (50–99% score)
Red = Failed or incomplete (<50% score)
Tips
• Complete wiring checks before signal simulation — there's no point simulating a signal if the wiring is wrong.
• Record test equipment serial numbers in the optional columns to maintain a traceable commissioning record for QA audits.
• Use N/A for checks that don't apply to a given loop type (e.g., calibration may not apply to a simple digital input).

## Loop Check Register
Loop Check Register — Summary Dashboard
Overall Progress |  |  |  |  | Check Category Pass Rates
Total Loops |  | 5 |  |  | Category | Pass Count | Total Applicable | Pass Rate
Loops Passed (100%) |  | 2 |  |  | Wiring Check | 5 | 5 | 100%
Loops with Failures |  | 3 |  |  | Signal Simulation | 3 | 4 | 75%
Loops In Progress |  | 0 |  |  | Calibration Check | 2 | 3 | 66.67%
Overall Pass Rate |  | 40% |  |  | Functional Test | 2 | 3 | 66.67%
Loop Identification | [5 empty] | Scored Check Items (Pass / Fail / N/A) |  |  |  |  | Results & Sign-Off |  |  | ▸ Optional Fields — Click [+] to expand
Item No. | Loop Tag | Instrument Description | P&ID Ref | System / Area | Instrument Type | Wiring Check | Signal Simulation | Calibration Check | Functional Test | Score (%) | Overall Status | Date Checked | Checked By | Expected Range | Actual Reading | Test Equipment Ref | Punch Items / Remarks
1 | FIT-101 | Flow Transmitter — Raw Water Inlet | P&ID-001 | Inlet Works | Flow | Pass | Pass | Pass | Pass | 100% | Pass | 2026-03-10 | M. Clarke | 0–50 l/s, 4–20mA | 12.4 mA @ 15.2 l/s | Fluke 789 S/N 4421
2 | LT-205 | Level Transmitter — Settlement Tank 2 | P&ID-005 | Primary Treatment | Level | Pass | Pass | Fail | N/A | 66.67% | Fail | 2026-03-11 | R. Evans | 0–4m, 4–20mA | 8.2 mA @ 1.05m | Beamex MC6 S/N 887 | Calibration out of tolerance — recalibrate required
3 | PT-310 | Pressure Transmitter — Backwash Header | P&ID-010 | Filtration | Pressure | Pass | Fail | N/A | N/A | 50% | Fail | 2026-03-12 | M. Clarke | 0–6 bar, 4–20mA | Signal stuck at 4mA | Fluke 789 S/N 4421 | Faulty transmitter — replacement on order
4 | TT-402 | Temperature Sensor — Digester 1 | P&ID-015 | Sludge Treatment | Temperature | Pass | Pass | Pass | Pass | 100% | Pass | 2026-03-13 | J. Patel | 0–80°C, PT100 | 37.2°C — matched reference | Isotech 935-14 S/N 102
5 | XV-501 | Isolation Valve — Chemical Dosing | P&ID-020 | Chemical Dosing | Valve | Pass | N/A | N/A | Fail | 50% | Fail | 2026-03-14 | R. Evans | Open/Close, 24VDC | Valve stuck — actuator fault | N/A | Actuator replacement needed — punch item #P-044
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50

## Terms of Use (hidden)
EBRORA — TERMS OF USE
This template is provided free of charge by Ebrora (ebrora.com) for personal and professional use.
1. LICENCE: You may use this template for your own projects. You may not resell, redistribute, or claim authorship of this template.
2. NO WARRANTY: This template is provided "as is" without warranty of any kind. Ebrora accepts no liability for errors, omissions, or losses arising from use of this template.
3. INTELLECTUAL PROPERTY: All design, layout, branding, and content remain the intellectual property of Ebrora.
4. MODIFICATIONS: You may modify this template for your own use. Modified versions may not be distributed or sold.
5. ATTRIBUTION: If you share outputs generated using this template, attribution to Ebrora (ebrora.com) is appreciated but not required.
6. SUPPORT: For queries, feedback, or to report errors, contact support@ebrora.com.
For our full range of professional construction management tools, visit ebrora.com.