## Cover
EBRORA
ebrora.com
P&ID Change Log &
Tag Consistency Matrix
Track P&ID revisions and verify tag-to-asset consistency
across drawings, SCADA, and the physical asset register.
This is a free template from Ebrora.
For our full range of professional-grade construction management tools, visit ebrora.com
© Ebrora 2026 — All rights reserved

## Instructions
How to Use This Template
Getting Started
1. | This template has two working sheets: the 'Tag Consistency Matrix' and the 'P&ID Change Log'.
2. | TAG CONSISTENCY MATRIX: Use this to verify that instrument/equipment tags are consistent across P&ID drawings, SCADA, the asset register, and site labels.
3. | Rows = individual tags (e.g., PMP-INL-001). Columns D onwards = sources to check against (P&ID Drawing, SCADA Tag List, Asset Register, Site Label, O&M Manual).
4. | In each intersection cell, select the status: Matched (tag is identical), Mismatch (tag exists but differs), Missing (tag not found in this source), or N/A.
5. | Column C shows the expected/master tag. The matrix helps you spot where naming has drifted between documents.
6. | The last column calculates a consistency score — the percentage of sources where the tag is 'Matched'.
7. | P&ID CHANGE LOG: Use this to track every revision or change to P&ID drawings, with the tag affected, change description, and approval.
8. | Each row is one change. Link it back to the Tag Consistency Matrix to verify the change has been reflected everywhere.
Colour Key
Light teal cells (#E8F6F7) = User input / editable fields
Dark navy headers (#1B2A4A) = Do not edit
Green = Matched (tag consistent) or 100% consistency score
Amber = Mismatch (tag differs between sources) or partial consistency
Red = Missing (tag not found) or low consistency score
Tips
Tip 1: | Complete the matrix BEFORE handover sign-off. Tag inconsistencies between P&IDs, SCADA, and O&M manuals cause months of confusion for operators.
Tip 2: | Use the P&ID Change Log to record every cloud/revision. When someone asks 'why does this valve have two different tag numbers', you'll have the answer.
Tip 3: | Filter the matrix by 'Mismatch' or 'Missing' to generate a punch list of tag corrections needed before as-built submission.

## Tag Consistency Matrix
Item No | System / Process Area | Master Tag | P&ID Drawing | SCADA Tag List | Asset Register | Site Label | O&M Manual | Consistency %
1 | Inlet Works | PMP-INL-001 | Matched | Matched | Matched | Matched | Matched | 100%
2 | Inlet Works | PMP-INL-002 | Matched | Matched | Mismatch | Matched | Mismatch | 60%
3 | Storm Water | VLV-SPS-014 | Matched | Missing | Matched | Matched | Missing | 60%
4 | Secondary Treatment | INS-FST-007 | Matched | Matched | Matched | Missing | Matched | 80%
5 | Secondary Treatment | PMP-RAS-002 | Matched | Mismatch | Matched | Matched | Matched | 80%
6 | Sludge Treatment | PMP-SLG-003 | Mismatch | Mismatch | Missing | Missing | N/A | 0%
7 | Inlet Works | SCR-INL-001 | Matched | Matched | Matched | Matched | Matched | 100%
8 | Storm Water | PEN-SPS-003 | Matched | Matched | Matched | Mismatch | Matched | 80%
SUMMARY | Total Tags: | 8 | 100% Consistent: | 2 | Mismatches Found: | 6 | Missing Tags: | 5

## P&ID Change Log
Change Ref | Date | P&ID Drawing No | Revision | Tag(s) Affected | Change Description | Change Type | Raised By | Approved By | Status | Notes
PID-001 | 2026-02-07 | P&ID-1001 | C | PMP-INL-001, PMP-INL-002 | Revised pump tag numbering from P-101/P-102 to PMP-INL-001/002 to align with site asset register convention. | Tag Change | A. Khan | S. Patel | Implemented | All sources updated — see matrix
PID-002 | 2026-02-22 | P&ID-3005 | B | VLV-SPS-014 | Added new storm tank penstock valve VLV-SPS-014 on storm return line to FST. DN600 rising spindle. | Equipment Addition | J. Davies | M. Thompson | Approved | Linked to design change DC-018
PID-003 | 2026-03-06 | P&ID-3005 | B | INS-DO-003 | Added dissolved oxygen probe INS-DO-003 on storm return liquor line upstream of FST inlet. | Instrument Addition | J. Davies |  | Under Review | Dependent on PID-002 approval
PID-004 | 2026-03-14 | P&ID-5002 | A | PMP-SLG-003 | Changed sludge transfer pump tag from P-501 to PMP-SLG-003. Existing P&ID still shows old tag. | Tag Change | R. Evans |  | Draft | SCADA and asset register not yet updated
SUMMARY | Total Changes: | 4 | Pending: | 2

## Terms of Use (hidden)
EBRORA — TERMS OF USE
This template is provided free of charge by Ebrora (ebrora.com) for personal and professional use.
LICENCE: You may use this template for your own projects. You may not resell, redistribute, or claim authorship of this template.
NO WARRANTY: This template is provided "as is" without warranty of any kind. Ebrora accepts no liability for errors, omissions, or losses arising from use of this template.
INTELLECTUAL PROPERTY: All design, layout, branding, and content remain the intellectual property of Ebrora.
MODIFICATIONS: You may modify this template for your own use. Modified versions may not be distributed or sold.
ATTRIBUTION: If you share outputs generated using this template, attribution to Ebrora (ebrora.com) is appreciated but not required.
SUPPORT: For queries, feedback, or to report errors, contact support@ebrora.com.
For our full range of professional construction management tools, visit ebrora.com.