## Cover
EBRORA
ebrora.com
SCADA / PLC
Change Log
Track and manage all software, firmware, and configuration changes
to SCADA and PLC systems with full version control and rollback records.
This is a free template from Ebrora.
For our full range of professional-grade construction management tools, visit ebrora.com
© Ebrora 2026 — All rights reserved

## Instructions
How to Use This Template
Getting Started
1. | Open the 'Change Log' sheet. Each row records a single change to a SCADA, PLC, RTU, or HMI system.
2. | Fill in the light teal cells — these are your input fields. Dark navy headers are fixed and should not be edited.
3. | Start with the Change Ref (auto-format: SCL-001, SCL-002 etc.) and the Date Raised.
4. | Select the System/Controller from the dropdown — this should match your site's asset register naming.
5. | Describe the change clearly in the Description column. Include what was changed, why, and what system behaviour is affected.
6. | Record the software/firmware version BEFORE and AFTER the change. This is critical for rollback.
7. | Select the Change Type (Configuration / Software / Firmware / HMI / Network) and Risk Level (Low / Medium / High / Critical).
8. | Track approval status through the workflow: Pending → Under Review → Approved → Implemented → Closed (or Rejected).
9. | Complete the Rollback Plan column for every change — even low-risk ones. A blank rollback plan is a failed audit.
10. | Use the optional columns (click [+] to expand) for FAT/SAT tracking, linked P&ID refs, and related CE/EW references.
Colour Key
Light teal cells (#E8F6F7) = User input / editable fields
Dark navy headers (#1B2A4A) = Do not edit
Green = Low risk or Approved/Implemented/Closed status
Amber = Medium risk or Under Review/Pending status
Red = High/Critical risk or Rejected status, or overdue pending items (>7 days)
Tips
Tip 1: | Filter by System/Controller to see all changes to a specific PLC or SCADA outstation — invaluable during commissioning.
Tip 2: | Before any energisation or wet commissioning, filter by Status = 'Pending' or 'Under Review' to catch unapproved changes.
Tip 3: | Print this log and include in your O&M handover pack. Auditors and operators will thank you.

## Change Log
Change Ref | Date Raised | System / Controller | Change Description | Version (From) | Version (To) | Change Type | Risk Level | Approval Status | Approved By | Implementation Date | Rollback Plan | Notes | Rollback Tested | FAT Required | SAT Required | Related P&ID Ref | Linked CE/EW Ref
SCL-001 | 2026-03-03 | PLC-WPS-01 (Inlet Works) | Modified high-level alarm setpoint on wet well pump station from 4.2m to 4.5m AOD to accommodate revised storm flow settings. Updated analog input scaling block. | v3.1.2 | v3.1.3 | Configuration | Low | Implemented | J. Davies | 2026-03-10 | Revert setpoint to 4.2m in FB_AnalogInput block. Backup stored: WPS01_v3.1.2_backup.zip | Linked to EW-044 | Yes | No | No | P&ID-1001-Rev.C | EW-044
SCL-002 | 2026-03-09 | SCADA Server (Primary) | Upgraded SCADA runtime from v8.2 to v8.3 to resolve historian data gap issue on SPS telemetry channels. Applied vendor patch KB-2024-118. | v8.2.0 | v8.3.0 | Software | High | Approved | S. Patel | 2026-03-14 | Full VM snapshot taken pre-upgrade. Rollback via VM restore to snapshot SCADA_PRE_v83. RTO: 30 mins. | FAT completed offsite at integrator | Yes | Yes | Yes | N/A
SCL-003 | 2026-03-16 | PLC-SPS-03 (Storm Tanks) | Added new interlock to prevent storm tank desludge pump running when return liquor DO > 2.5 mg/L. New function block FB_StormInterlock added to main program. | v2.0.0 | v2.1.0 | Software | Medium | Under Review |  |  | Remove FB_StormInterlock call from OB1. Revert to v2.0.0 project file from backup server. |  | No | Yes | Yes | P&ID-3005-Rev.B | CE-012
SCL-004 | 2026-03-21 | HMI-MCR-01 (Main Control) | Updated mimic display for new storm tank interlock status. Added alarm banner for DO interlock trip. Colour coding per site alarm philosophy. | v1.4.0 | v1.5.0 | HMI | Low | Pending |  |  | Restore previous HMI project from HMI_MCR01_v1.4.0_backup. Re-download to panel. | Dependent on SCL-003 approval | No | No | No | P&ID-3005-Rev.B
SCL-005 | 2026-02-22 | RTU-BH-07 (Borehole 7) | Firmware update on RTU communications module to resolve intermittent Modbus timeout errors. Vendor-issued patch FW-2024-003. | FW-1.2.0 | FW-1.2.1 | Firmware | Critical | Closed | M. Thompson | 2026-03-02 | Flash previous firmware FW-1.2.0 via JTAG connector. Procedure doc: RTU_FW_Rollback_SOP.pdf | Resolved site telemetry dropout issue | Yes | No | No | N/A | EW-039
SUMMARY | Total Changes: | 5 | Pending/Under Review: | 2 | Rejected: | 0 | High/Critical Risk: | 2

## Terms of Use (hidden)
EBRORA — TERMS OF USE
This template is provided free of charge by Ebrora (ebrora.com) for personal and professional use.
LICENCE: You may use this template for your own projects. You may not resell, redistribute, or claim authorship of this template.
NO WARRANTY: This template is provided "as is" without warranty of any kind. Ebrora accepts no liability for errors, omissions, or losses arising from use of this template.
INTELLECTUAL PROPERTY: All design, layout, branding, and content remain the intellectual property of Ebrora.
MODIFICATIONS: You may modify this template for your own use. Modified versions may not be distributed or sold.
ATTRIBUTION: If you share outputs generated using this template, attribution to Ebrora (ebrora.com) is appreciated but not required.
SUPPORT: For queries, feedback, or to report errors, contact support@ebrora.com.
For our full range of professional construction management tools, visit ebrora.com.