Air Tightness Test Preparation

Checklist

| Document Ref: | Enter reference | Revision: | Enter revision |
| --- | --- | --- | --- |
| Project Name: | Enter project name | Contract No: | Enter contract number |
| Date: | DD / MM / YYYY | Prepared By: | Name and role |
| Approved By: | Name and role | Test Date: | Enter details |

# 1. Building Details

| Building / Plot: | Enter building or plot reference |
| --- | --- |
| Building Type: | e.g. Residential dwelling, commercial office, school, industrial unit |
| Floor Area (m²): | m² (treated floor area) |
| Volume (m³): | m³ (internal volume for test) |
| Target Air Permeability: | m³/(h.m²) at 50 Pa (e.g. 5.0 for Part L, or design target) |
| Design Air Permeability: | m³/(h.m²) at 50 Pa (from SAP/SBEM calculation) |
| Testing Company: | Enter UKAS accredited testing company name |
| Test Standard: | BS EN ISO 9972 (ATTMA TSL1 for dwellings or TSL2 for non-dwellings) |

# 2. Pre-Test Preparation Checklist

| No. | Check Item | Pass | Fail | N/A | Initials |
| --- | --- | --- | --- | --- | --- |
| 1 | All external doors and windows installed, closed, and latched |  |  |  |  |
| 2 | All internal doors open (to create single test zone) |  |  |  |  |
| 3 | Loft hatches closed and sealed (if within the air barrier) |  |  |  |  |
| 4 | Letter box flaps closed or temporarily sealed |  |  |  |  |
| 5 | Trickle vents closed |  |  |  |  |
| 6 | Mechanical ventilation systems switched off and sealed (MVHR, MEV, extract fans) |  |  |  |  |
| 7 | Extract fan grilles and ducting temporarily sealed |  |  |  |  |
| 8 | Cooker hood extract duct temporarily sealed |  |  |  |  |
| 9 | Tumble dryer vent temporarily sealed |  |  |  |  |
| 10 | Bathroom / WC passive stack vents temporarily sealed |  |  |  |  |
| 11 | Flue terminals temporarily sealed (open flues, wood burners, gas fires) |  |  |  |  |
| 12 | Gas meter / electricity meter cupboard doors closed |  |  |  |  |
| 13 | Overflow pipes sealed (if penetrating the air barrier) |  |  |  |  |
| 14 | Waste pipe traps filled with water (all sinks, baths, showers, WCs flushed) |  |  |  |  |
| 15 | Floor drain traps filled with water |  |  |  |  |
| 16 | Service penetrations sealed (gas, electric, water, telecoms, drainage) |  |  |  |  |
| 17 | All plasterboard joints and junctions taped and finished |  |  |  |  |
| 18 | Sealant applied to window and door frame perimeters |  |  |  |  |
| 19 | Membrane / air barrier continuous and undamaged (visual check) |  |  |  |  |
| 20 | Smoke pencil test completed on suspect areas before formal test |  |  |  |  |
| 21 | Heating system operational (building at stable temperature) |  |  |  |  |
| 22 | Wind speed acceptable for testing (< 6 m/s or as per ATTMA guidance) |  |  |  |  |

# 3. Known Risk Areas

| No. | Potential Leakage Path | Location | Sealed? | Comments |
| --- | --- | --- | --- | --- |
| 1 |  |  | Y/N |  |
| 2 |  |  | Y/N |  |
| 3 |  |  | Y/N |  |
| 4 |  |  | Y/N |  |
| 5 |  |  | Y/N |  |
| 6 |  |  | Y/N |  |
| 7 |  |  | Y/N |  |
| 8 |  |  | Y/N |  |
| 9 |  |  | Y/N |  |
| 10 |  |  | Y/N |  |

# 4. Test Results (completed by tester)

| Air Permeability Result: | m³/(h.m²) at 50 Pa |
| --- | --- |
| Target Achieved? | Yes / No |
| Test Certificate Ref: | Enter ATTMA certificate reference |
| Re-Test Required? | Yes / No – if Yes, state remedial actions |

# 5. Sign-Off

| Site Manager |  | Air Tightness Tester |  |
| --- | --- | --- | --- |
| Name: | Print name | Name: | Print name |
| Signature: |  | Signature: |  |
| Date: | DD / MM / YYYY | Date: | DD / MM / YYYY |

# 6. Document Control

| Revision | Date | Description of Change | Author | Approved By |
| --- | --- | --- | --- | --- |
| 01 | DD/MM/YYYY | Initial issue |  |  |
|  | DD/MM/YYYY |  |  |  |
|  | DD/MM/YYYY |  |  |  |