Chemical Clean and Flushing

Record

| Document Ref: | Enter reference | Revision: | Enter revision |
| --- | --- | --- | --- |
| Project Name: | Enter project name | Contract No: | Enter contract number |
| Date: | DD / MM / YYYY | Carried Out By: | Name and company |
| Witnessed By: | Name and role | Approved By: | Name and role |

# 1. System Details

| System Name / Ref: | e.g. LTHW heating system, CHW system, process pipework loop 3 |
| --- | --- |
| System Description: | Describe the system being cleaned: pipe materials, sizes, length, equipment served |
| P&ID / Drawing Ref: | Enter relevant P&ID or schematic drawing numbers |
| Pipe Material: | e.g. Mild steel, copper, stainless steel, GRP, PE, ductile iron |
| System Volume (approx.): | litres or m³ |
| Design Operating Temperature: | °C |
| Design Operating Pressure: | bar |
| Cleaning Specification Ref: | e.g. BSRIA BG 29, project specification clause |

# 2. Pre-Clean Checklist

| No. | Check Item | Yes | No | N/A | Initials |
| --- | --- | --- | --- | --- | --- |
| 1 | System pressure tested and leak-free before cleaning commences |  |  |  |  |
| 2 | All strainers, Y-strainers, and temporary filters installed |  |  |  |  |
| 3 | Sensitive equipment isolated or bypassed (flow meters, control valves, heat exchangers) |  |  |  |  |
| 4 | Chemical dosing equipment set up and connected |  |  |  |  |
| 5 | Water supply connected and adequate for filling and flushing |  |  |  |  |
| 6 | Drain points identified and discharge route approved (trade effluent consent if required) |  |  |  |  |
| 7 | COSHH assessment available for all cleaning chemicals |  |  |  |  |
| 8 | PPE available for chemical handling (gloves, goggles, overalls, face shield) |  |  |  |  |
| 9 | Emergency spill kit and eye wash station available |  |  |  |  |
| 10 | All operatives briefed on the cleaning procedure and chemical hazards |  |  |  |  |
| 11 | Temporary flushing connections installed where required |  |  |  |  |
| 12 | Air vents opened and system fully vented before filling |  |  |  |  |

# 3. Chemical Clean Details

| Cleaning Chemical: | Enter chemical name and product reference |
| --- | --- |
| Chemical Manufacturer: | Enter manufacturer name |
| Chemical Batch No: | Enter batch number |
| Dosing Concentration: | e.g. % by volume, ppm, mg/l |
| Volume of Chemical Used: | litres |
| Circulation Temperature: | °C (if heated circulation required) |
| Circulation Duration: | hours |
| Circulation Start Time: | Date: DD/MM/YYYY Time: HH:MM |
| Circulation End Time: | Date: DD/MM/YYYY Time: HH:MM |
| Flow Velocity Achieved: | m/s (minimum 1.0 m/s recommended for effective cleaning) |

# 4. Flushing Record

| Flush No. | Date | Start Time | End Time | Duration | Water Vol m³ | Observations |
| --- | --- | --- | --- | --- | --- | --- |
| Flush 1 | DD/MM | HH:MM | HH:MM | hrs | m³ |  |
| Flush 2 | DD/MM | HH:MM | HH:MM | hrs | m³ |  |
| Flush 3 | DD/MM | HH:MM | HH:MM | hrs | m³ |  |
| Flush 4 | DD/MM | HH:MM | HH:MM | hrs | m³ |  |
| Flush 5 | DD/MM | HH:MM | HH:MM | hrs | m³ |  |
| Flush 6 | DD/MM | HH:MM | HH:MM | hrs | m³ |  |
| Flush 7 | DD/MM | HH:MM | HH:MM | hrs | m³ |  |
| Flush 8 | DD/MM | HH:MM | HH:MM | hrs | m³ |  |

# 5. Water Quality Monitoring

| Sample | Date/Time | pH | TDS ppm | Turbidity NTU | Iron ppm | Conductivity | Appearance |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Pre-clean (fill water) |  |  |  |  |  | µS/cm |  |
| During clean (1 hr) |  |  |  |  |  | µS/cm |  |
| During clean (mid-point) |  |  |  |  |  | µS/cm |  |
| End of clean |  |  |  |  |  | µS/cm |  |
| Post-flush 1 |  |  |  |  |  | µS/cm |  |
| Post-flush 2 |  |  |  |  |  | µS/cm |  |
| Post-flush 3 |  |  |  |  |  | µS/cm |  |
| Final (acceptance) |  |  |  |  |  | µS/cm |  |

# 6. Acceptance Criteria

| Parameter | Acceptance Limit | Final Result | Pass / Fail |
| --- | --- | --- | --- |
| pH | 6.5 – 8.5 (or as specified) |  | P / F |
| Total dissolved solids (TDS) | < 100 ppm above mains water (or as specified) |  | P / F |
| Turbidity | < 5 NTU (or as specified) |  | P / F |
| Iron content | < 1 ppm (or as specified) |  | P / F |
| Appearance | Clear, free from debris and discolouration |  | P / F |
| Strainer debris | Clean – no significant material on strainer mesh |  | P / F |

# 7. Post-Clean Treatment

| Inhibitor Chemical: | Enter inhibitor name and product reference |
| --- | --- |
| Inhibitor Manufacturer: | Enter manufacturer name |
| Dosing Concentration: | ppm or ml per litre |
| Date Dosed: | DD / MM / YYYY |
| Inhibitor Test Result: | ppm (confirm within recommended range) |
| Biocide Dosed? | Yes / No – state product and concentration |
| System Left Full and Pressurised? | Yes / No |

# 8. Waste Disposal

| Waste Water Disposal Method: | e.g. Foul drain (with consent), tanker removal, treatment on site |
| --- | --- |
| Trade Effluent Consent Ref: | Enter consent reference or N/A |
| Volume of Waste Water: | m³ |
| Neutralisation Required? | Yes / No – pH adjusted to 6–9 before discharge |
| Waste Transfer Note Ref: | Enter WTN reference or N/A |

# 9. Sign-Off

This record confirms that the chemical clean and flushing has been completed in accordance with the specified procedure. Final water quality results meet the acceptance criteria and the system is ready for commissioning.

| Cleaning Contractor |  | Engineer / Witness |  |
| --- | --- | --- | --- |
| Name: | Print name | Name: | Print name |
| Company: | Enter company | Position: | Enter role |
| Signature: |  | Signature: |  |
| Date: | DD / MM / YYYY | Date: | DD / MM / YYYY |

# 10. Document Control

| Revision | Date | Description of Change | Author | Approved By |
| --- | --- | --- | --- | --- |
| 01 | DD/MM/YYYY | Initial issue |  |  |
|  | DD/MM/YYYY |  |  |  |
|  | DD/MM/YYYY |  |  |  |