Power Factor Correction

Test Record

| Document Ref: | Enter reference | Revision: | Enter revision |
| --- | --- | --- | --- |
| Project Name: | Enter project name | Contract No: | Enter contract number |
| Date of Test: | DD / MM / YYYY | Tested By: | Name and company |
| Witnessed By: | Name and role | Approved By: | Name and role |

# 1. PFC Equipment Details

| PFC Panel Tag / Ref: | Enter asset tag number |
| --- | --- |
| Manufacturer: | Enter manufacturer name |
| Model / Type: | Enter model number |
| Serial Number: | Enter serial number |
| Total Rated Capacity: | kVAr |
| Number of Steps: | Enter number of capacitor steps |
| Step Sizes (kVAr): | e.g. 25, 25, 50, 50, 100 kVAr |
| System Voltage: | e.g. 400V, 3-phase |
| Detuning Reactor Fitted? | Yes / No – if Yes, state tuning frequency (e.g. 189 Hz / 7%) |
| Controller Type: | Enter PFC controller manufacturer and model |
| Target Power Factor: | e.g. 0.95 lagging, 0.98 lagging, unity |
| Location / Board: | Enter panel location and associated switchboard |
| Drawing Reference: | Enter SLD and PFC panel drawing references |

# 2. Pre-Test Checks

| No. | Test / Check Item | Pass | Fail | N/A | Initials |
| --- | --- | --- | --- | --- | --- |
| 1 | PFC panel installed in accordance with manufacturer’s instructions |  |  |  |  |
| 2 | All electrical connections torque-checked and recorded |  |  |  |  |
| 3 | Insulation resistance tests completed on capacitor circuits |  |  |  |  |
| 4 | CT ratio and polarity verified for PFC controller input |  |  |  |  |
| 5 | CT secondary correctly wired to PFC controller (correct phase) |  |  |  |  |
| 6 | Controller programmed with correct CT ratio and system parameters |  |  |  |  |
| 7 | Target power factor (cos φ) set on controller |  |  |  |  |
| 8 | Step switching delay times configured correctly |  |  |  |  |
| 9 | Discharge resistors fitted to each capacitor bank (verify < 50V in 1 min) |  |  |  |  |
| 10 | Fuses / MCCBs correctly rated for each capacitor step |  |  |  |  |
| 11 | Ventilation adequate in PFC panel enclosure (temperature < 40°C) |  |  |  |  |
| 12 | Earth bonding connections verified |  |  |  |  |
| 13 | Warning labels displayed (capacitors may retain charge) |  |  |  |  |

# 3. Capacitor Bank Test Results

| Step | Rating kVAr | Capacitance µF | Measured µF | Current A (design) | Current A (meas.) | Insulation MΩ | Discharge OK? | Pass? |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | kVAr | µF | µF | A | A | MΩ | Y/N | Y/N |
| 2 | kVAr | µF | µF | A | A | MΩ | Y/N | Y/N |
| 3 | kVAr | µF | µF | A | A | MΩ | Y/N | Y/N |
| 4 | kVAr | µF | µF | A | A | MΩ | Y/N | Y/N |
| 5 | kVAr | µF | µF | A | A | MΩ | Y/N | Y/N |
| 6 | kVAr | µF | µF | A | A | MΩ | Y/N | Y/N |
| 7 | kVAr | µF | µF | A | A | MΩ | Y/N | Y/N |
| 8 | kVAr | µF | µF | A | A | MΩ | Y/N | Y/N |

# 4. Controller Stepping Test

Verify that the PFC controller switches steps in and out correctly in response to changing load conditions.

| Test | Load Condition | PF Before | Steps In | PF After | kVAr In | kW Load | Comments |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Low load (< 25%) |  |  |  |  |  |  |
| 2 | Medium load (50%) |  |  |  |  |  |  |
| 3 | High load (75%) |  |  |  |  |  |  |
| 4 | Full load (100%) |  |  |  |  |  |  |
| 5 | Reducing load |  |  |  |  |  |  |
| 6 | No load |  |  |  |  |  |  |

# 5. Harmonic Assessment

| THD Voltage (Before PFC): | % THDv |
| --- | --- |
| THD Voltage (After PFC): | % THDv |
| THD Current (Before PFC): | % THDi |
| THD Current (After PFC): | % THDi |
| Detuning Reactor Effective? | Yes / No – no resonance observed at any load condition |
| Harmonic Measurement Instrument: | Enter make, model, and calibration date |

# 6. Overall Test Results

| Parameter | Before PFC | After PFC | Target |
| --- | --- | --- | --- |
| Power factor (cos φ) |  |  |  |
| Reactive power (kVAr) |  |  |  |
| Active power (kW) |  |  |  |
| Apparent power (kVA) |  |  |  |
| Supply current (A) |  |  |  |
| Supply voltage (V) |  |  |  |
| THDv (%) |  |  |  |
| THDi (%) |  |  |  |

# 7. Post-Test Checklist

| No. | Test / Check Item | Pass | Fail | N/A | Initials |
| --- | --- | --- | --- | --- | --- |
| 1 | Target power factor achieved under all tested load conditions |  |  |  |  |
| 2 | No hunting or rapid switching observed on the controller |  |  |  |  |
| 3 | No leading power factor condition observed at any load |  |  |  |  |
| 4 | All capacitor steps switching in and out correctly |  |  |  |  |
| 5 | No excessive heating of capacitors, contactors, or reactors |  |  |  |  |
| 6 | No audible buzzing or humming from detuning reactors beyond normal |  |  |  |  |
| 7 | Controller display showing correct values and no fault alarms |  |  |  |  |
| 8 | Alarms tested: over-voltage, under-voltage, over-temperature, harmonic |  |  |  |  |
| 9 | DNO reactive power charges expected to reduce (commercial benefit confirmed) |  |  |  |  |
| 10 | PFC panel labelled with rated capacity and warning signage |  |  |  |  |

# 8. Snags and Actions

| No. | Issue Description | Action Required | Owner | Status |
| --- | --- | --- | --- | --- |
| 1 |  |  |  | Open / Closed |
| 2 |  |  |  | Open / Closed |
| 3 |  |  |  | Open / Closed |
| 4 |  |  |  | Open / Closed |
| 5 |  |  |  | Open / Closed |

# 9. Sign-Off

| Test Engineer |  | Witness / Client Rep |  |
| --- | --- | --- | --- |
| Name: | Print name | Name: | Print name |
| Company: | Enter company | Position: | Enter role |
| Signature: |  | Signature: |  |
| Date: | DD / MM / YYYY | Date: | DD / MM / YYYY |

# 10. Document Control

| Revision | Date | Description of Change | Author | Approved By |
| --- | --- | --- | --- | --- |
| 01 | DD/MM/YYYY | Initial issue |  |  |
|  | DD/MM/YYYY |  |  |  |
|  | DD/MM/YYYY |  |  |  |