UPS and Battery System

Commissioning Record

| Document Ref: | Enter reference | Revision: | Enter revision |
| --- | --- | --- | --- |
| Project Name: | Enter project name | Contract No: | Enter contract number |
| Date: | DD / MM / YYYY | Commissioned By: | Name and company |
| Witnessed By: | Name and role | Approved By: | Name and role |

# 1. UPS Equipment Details

| UPS Tag / Reference: | Enter asset tag number |
| --- | --- |
| Manufacturer: | Enter manufacturer name |
| Model: | Enter model number |
| Serial Number: | Enter serial number |
| Rated Output (kVA / kW): | Enter rated capacity |
| Input Voltage / Phases: | e.g. 400V 3-phase, 230V single-phase |
| Output Voltage: | e.g. 230V single-phase, 400V 3-phase |
| UPS Topology: | e.g. Online double conversion, line-interactive, standby |
| Bypass Type: | e.g. Internal static bypass, external maintenance bypass |
| Location / Room: | Enter building and room |
| Drawing Reference: | Enter SLD and layout drawing references |

# 2. Battery Details

| Battery Type: | e.g. VRLA (sealed lead-acid), lithium-ion, nickel-cadmium, flooded |
| --- | --- |
| Battery Manufacturer: | Enter manufacturer name |
| Battery Model: | Enter model / part number |
| Number of Battery Strings: | Enter number of parallel strings |
| Cells / Blocks Per String: | Enter number |
| Nominal Battery Voltage: | VDC |
| Capacity (Ah): | Enter Ah rating at specified discharge rate |
| Designed Autonomy: | e.g. 10 minutes, 30 minutes, 1 hour at full load |
| Date of Manufacture: | DD / MM / YYYY |
| Battery Room Ventilation: | Natural / Mechanical – adequate for hydrogen dissipation? |

# 3. Pre-Commissioning Checks

| No. | Test / Check Item | Pass | Fail | N/A | Initials |
| --- | --- | --- | --- | --- | --- |
| 1 | UPS installed in accordance with manufacturer's installation manual |  |  |  |  |
| 2 | All electrical connections torque-checked and recorded |  |  |  |  |
| 3 | Input and output cables correctly sized and terminated |  |  |  |  |
| 4 | Earth bonding connections verified |  |  |  |  |
| 5 | Insulation resistance tests completed on input, output, and battery circuits |  |  |  |  |
| 6 | Battery blocks / cells correctly installed and interconnected |  |  |  |  |
| 7 | Battery terminal connections torque-checked (value recorded below) |  |  |  |  |
| 8 | Battery electrolyte levels checked (flooded cells) or VRLA seals intact |  |  |  |  |
| 9 | Battery room / cabinet ventilation confirmed adequate |  |  |  |  |
| 10 | UPS room temperature within manufacturer's operating range |  |  |  |  |
| 11 | External maintenance bypass switch installed and labelled |  |  |  |  |
| 12 | All protective devices (MCBs, fuses) correctly rated and fitted |  |  |  |  |
| 13 | SCADA / BMS alarm connections wired and tested |  |  |  |  |
| 14 | Emergency power off (EPO) button installed, wired, and tested |  |  |  |  |

# 4. Commissioning Tests

| No. | Test / Check Item | Pass | Fail | N/A | Initials |
| --- | --- | --- | --- | --- | --- |
| 1 | Mains supply energised – input voltage and phase rotation verified |  |  |  |  |
| 2 | UPS powered up in normal mode – no alarms or faults displayed |  |  |  |  |
| 3 | Output voltage and frequency measured and within tolerance |  |  |  |  |
| 4 | Battery float charge voltage verified at each cell / block |  |  |  |  |
| 5 | Battery equalise (boost) charge initiated and monitored |  |  |  |  |
| 6 | Transfer to battery mode tested (simulate mains failure) |  |  |  |  |
| 7 | Output maintained within specification during battery transfer |  |  |  |  |
| 8 | Transfer time measured (online UPS: 0ms, line-interactive: < 5ms) |  |  |  |  |
| 9 | Battery discharge test conducted under load (autonomy verified) |  |  |  |  |
| 10 | Actual autonomy achieved matches or exceeds design requirement |  |  |  |  |
| 11 | Automatic retransfer to mains tested on mains restoration |  |  |  |  |
| 12 | Static bypass operation tested (manual transfer to bypass) |  |  |  |  |
| 13 | External maintenance bypass operation tested (for maintenance isolation) |  |  |  |  |
| 14 | Overload transfer to bypass tested at rated overload percentage |  |  |  |  |
| 15 | All alarm outputs verified: mains fail, battery low, overload, fault, bypass |  |  |  |  |
| 16 | Remote monitoring / SNMP card communication verified (if applicable) |  |  |  |  |
| 17 | Harmonic distortion (THDi and THDv) measured and within specification |  |  |  |  |

# 5. Test Measurements

| Parameter | Specification | Measured | Pass / Fail |
| --- | --- | --- | --- |
| Input voltage L1-L2-L3 (V) |  |  | P / F |
| Input frequency (Hz) |  |  | P / F |
| Output voltage (V) |  |  | P / F |
| Output frequency (Hz) |  |  | P / F |
| Load at time of test (kVA / kW) |  |  | P / F |
| Load as % of rated capacity |  |  | P / F |
| Battery float voltage total (VDC) |  |  | P / F |
| Battery float voltage per cell (VDC) |  |  | P / F |
| Battery discharge start voltage (VDC) |  |  | P / F |
| Battery end voltage at cutoff (VDC) |  |  | P / F |
| Battery autonomy achieved (minutes) |  |  | P / F |
| Transfer time mains to battery (ms) |  |  | P / F |
| Transfer time battery to mains (ms) |  |  | P / F |
| Output THDv (%) |  |  | P / F |
| Input THDi (%) |  |  | P / F |
| Ambient temperature (°C) |  |  | P / F |

# 6. Snags and Actions

| No. | Issue Description | Action Required | Owner | Status |
| --- | --- | --- | --- | --- |
| 1 |  |  |  | Open / Closed |
| 2 |  |  |  | Open / Closed |
| 3 |  |  |  | Open / Closed |
| 4 |  |  |  | Open / Closed |
| 5 |  |  |  | Open / Closed |
| 6 |  |  |  | Open / Closed |

# 7. Sign-Off

This record confirms that the UPS and battery system has been commissioned in accordance with the manufacturer's procedures and project specification. All tests have been completed and the results are within the specified tolerances.

| Commissioning Engineer |  | Witness / Client Rep |  |
| --- | --- | --- | --- |
| Name: | Print name | Name: | Print name |
| Company: | Enter company | Position: | Enter role |
| Signature: |  | Signature: |  |
| Date: | DD / MM / YYYY | Date: | DD / MM / YYYY |

# 8. Document Control

| Revision | Date | Description of Change | Author | Approved By |
| --- | --- | --- | --- | --- |
| 01 | DD/MM/YYYY | Initial issue |  |  |
|  | DD/MM/YYYY |  |  |  |
|  | DD/MM/YYYY |  |  |  |