Telemetry Outstation

Commissioning Record

| Document Ref: | Enter reference | Revision: | Enter revision |
| --- | --- | --- | --- |
| Project Name: | Enter project name | Contract No: | Enter contract number |
| Date: | DD / MM / YYYY | Commissioned By: | Name and company |
| Witnessed By: | Name and role | Approved By: | Name and role |

# 1. Outstation Details

| Site / Station Name: | Enter site or pumping station name |
| --- | --- |
| Outstation Tag / Ref: | Enter outstation reference number |
| Manufacturer: | Enter RTU / outstation manufacturer |
| Model: | Enter model number |
| Serial Number: | Enter serial number |
| Firmware Version: | Enter firmware version installed |
| Location / Panel Ref: | Enter panel or kiosk reference |
| Drawing Reference: | Enter wiring diagram and schematic drawing references |

# 2. Communication Details

| Communication Method: | e.g. GPRS, 3G/4G, fibre, radio, leased line, satellite |
| --- | --- |
| SIM Card Number (if cellular): | Enter SIM ICCID number |
| IP Address: | Enter assigned IP address |
| Subnet Mask: | Enter subnet mask |
| Gateway: | Enter default gateway |
| Protocol: | e.g. DNP3, Modbus TCP, IEC 60870-5-104, MQTT |
| Master Station Address: | Enter master / SCADA host address |
| Outstation Address: | Enter outstation / slave address |
| Polling Interval: | e.g. 15 seconds, 30 seconds, 60 seconds |
| Signal Strength (dBm): | Enter cellular signal strength reading |

# 3. Pre-Commissioning Checks

| No. | Test / Check Item | Pass | Fail | N/A | Initials |
| --- | --- | --- | --- | --- | --- |
| 1 | Outstation installed in accordance with manufacturer's specification |  |  |  |  |
| 2 | All wiring terminated correctly and labelled per wiring diagram |  |  |  |  |
| 3 | Power supply connected and voltage verified (24VDC / 230VAC as applicable) |  |  |  |  |
| 4 | Battery backup installed, charged, and autonomy verified |  |  |  |  |
| 5 | Antenna installed at correct position and orientation (cellular / radio) |  |  |  |  |
| 6 | Surge protection devices (SPDs) installed on power and signal lines |  |  |  |  |
| 7 | Earth bonding connections verified |  |  |  |  |
| 8 | All I/O modules correctly installed and addressed |  |  |  |  |
| 9 | Configuration file loaded and version confirmed |  |  |  |  |
| 10 | Clock synchronised (NTP or GPS time source) |  |  |  |  |
| 11 | Panel internals clean, tidy, and cable management completed |  |  |  |  |
| 12 | Panel door seal and IP rating verified |  |  |  |  |

# 4. Digital Input (DI) Verification

| No. | DI Address | Signal Description | Source Tag | Forced State | SCADA Correct? | Comments |
| --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  |  | 0 / 1 | Y / N |  |
| 2 |  |  |  | 0 / 1 | Y / N |  |
| 3 |  |  |  | 0 / 1 | Y / N |  |
| 4 |  |  |  | 0 / 1 | Y / N |  |
| 5 |  |  |  | 0 / 1 | Y / N |  |
| 6 |  |  |  | 0 / 1 | Y / N |  |
| 7 |  |  |  | 0 / 1 | Y / N |  |
| 8 |  |  |  | 0 / 1 | Y / N |  |
| 9 |  |  |  | 0 / 1 | Y / N |  |
| 10 |  |  |  | 0 / 1 | Y / N |  |
| 11 |  |  |  | 0 / 1 | Y / N |  |
| 12 |  |  |  | 0 / 1 | Y / N |  |

# 5. Analogue Input (AI) Verification

| No. | AI Addr | Signal Description | Source Tag | Simulated | SCADA Value | Error % | Pass? |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  |  | mA / V |  | % | Y / N |
| 2 |  |  |  | mA / V |  | % | Y / N |
| 3 |  |  |  | mA / V |  | % | Y / N |
| 4 |  |  |  | mA / V |  | % | Y / N |
| 5 |  |  |  | mA / V |  | % | Y / N |
| 6 |  |  |  | mA / V |  | % | Y / N |
| 7 |  |  |  | mA / V |  | % | Y / N |
| 8 |  |  |  | mA / V |  | % | Y / N |
| 9 |  |  |  | mA / V |  | % | Y / N |
| 10 |  |  |  | mA / V |  | % | Y / N |

# 6. Digital Output (DO) / Control Verification

| No. | DO Address | Control Description | Target Tag | Command Sent | Device Operated? | Comments |
| --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  |  | Open/Close | Y / N |  |
| 2 |  |  |  | Open/Close | Y / N |  |
| 3 |  |  |  | Open/Close | Y / N |  |
| 4 |  |  |  | Open/Close | Y / N |  |
| 5 |  |  |  | Open/Close | Y / N |  |
| 6 |  |  |  | Open/Close | Y / N |  |
| 7 |  |  |  | Open/Close | Y / N |  |
| 8 |  |  |  | Open/Close | Y / N |  |

# 7. Alarm and Event Tests

| No. | Alarm Description | Trigger Value | Alarm Received at SCADA? | Correct Priority? | Comments |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  | Y / N | Y / N |  |
| 2 |  |  | Y / N | Y / N |  |
| 3 |  |  | Y / N | Y / N |  |
| 4 |  |  | Y / N | Y / N |  |
| 5 |  |  | Y / N | Y / N |  |
| 6 |  |  | Y / N | Y / N |  |
| 7 |  |  | Y / N | Y / N |  |
| 8 |  |  | Y / N | Y / N |  |
| 9 |  |  | Y / N | Y / N |  |
| 10 |  |  | Y / N | Y / N |  |

# 8. Communication Tests

| No. | Test / Check Item | Pass | Fail | N/A | Initials |
| --- | --- | --- | --- | --- | --- |
| 1 | Communication established between outstation and master station |  |  |  |  |
| 2 | Data polling confirmed at the specified interval |  |  |  |  |
| 3 | All DI, AI, DO, and AO points visible and updating at master station |  |  |  |  |
| 4 | Communication loss alarm tested (disconnect antenna / cable) |  |  |  |  |
| 5 | Communication restored automatically after loss (auto-reconnect) |  |  |  |  |
| 6 | Data logging confirmed at outstation (local buffer) |  |  |  |  |
| 7 | Logged data uploaded to master station after communication restored |  |  |  |  |
| 8 | Time stamp accuracy verified on all events and alarms |  |  |  |  |
| 9 | Redundant communication path tested (if dual path configured) |  |  |  |  |
| 10 | Remote firmware update capability verified (if applicable) |  |  |  |  |

# 9. Snags and Actions

| No. | Issue Description | Action Required | Owner | Status |
| --- | --- | --- | --- | --- |
| 1 |  |  |  | Open / Closed |
| 2 |  |  |  | Open / Closed |
| 3 |  |  |  | Open / Closed |
| 4 |  |  |  | Open / Closed |
| 5 |  |  |  | Open / Closed |
| 6 |  |  |  | Open / Closed |

# 10. Sign-Off

| Commissioning Engineer |  | Client / Telemetry Team |  |
| --- | --- | --- | --- |
| Name: | Print name | Name: | Print name |
| Company: | Enter company | Position: | Enter role |
| Signature: |  | Signature: |  |
| Date: | DD / MM / YYYY | Date: | DD / MM / YYYY |

# 11. Document Control

| Revision | Date | Description of Change | Author | Approved By |
| --- | --- | --- | --- | --- |
| 01 | DD/MM/YYYY | Initial issue |  |  |
|  | DD/MM/YYYY |  |  |  |
|  | DD/MM/YYYY |  |  |  |