Air Test Record for Drainage

| Document Ref: | Enter reference | Revision: | Enter revision |
| --- | --- | --- | --- |
| Project Name: | Enter project name | Contract No: | Enter contract number |
| Date of Test: | DD / MM / YYYY | Tested By: | Name and company |
| Witnessed By: | Name and role | Approved By: | Name and role |

# 1. Pipeline Details

| Pipeline / Sewer Ref: | Enter pipeline reference from drawings |
| --- | --- |
| Test Section: | e.g. MH 101 to MH 102, from connection to outfall |
| Pipe Material: | e.g. Vitrified clay, uPVC, PP, PE, GRP, concrete |
| Nominal Diameter (DN): | mm |
| Test Section Length: | metres |
| Number of Joints in Section: | Enter number |
| Joint Type: | e.g. Push-fit, solvent weld, mechanical coupling, fusion welded |
| Depth to Invert: | metres (at upstream and downstream ends) |
| Drawing Reference: | Enter drainage layout drawing number and revision |
| Applicable Standard: | WIS 4-34-04 (Water Industry Specification) / BS EN 1610 |

# 2. Test Equipment

| Air Test Equipment: | Enter make and model of air test kit |
| --- | --- |
| Serial Number: | Enter serial number |
| Calibration Date: | DD / MM / YYYY |
| Calibration Certificate Ref: | Enter certificate reference |
| Stopper / Plug Type: | e.g. Inflatable bag stopper, mechanical plug, test cap |

# 3. Test Parameters

Per WIS 4-34-04 / BS EN 1610: Pressurise to 100mm water gauge (10 mbar). Allow pressure to stabilise. Start timing when pressure drops to 75mm (7.5 mbar). The test passes if the pressure does not drop below 50mm (5 mbar) within the permitted time.

| Initial Test Pressure: | 100 mm water gauge (10 mbar) |
| --- | --- |
| Stabilisation Period: | 5 minutes (or until pressure steady) |
| Start Pressure (timing begins): | 75 mm water gauge (7.5 mbar) |
| Minimum Acceptable Pressure: | 50 mm water gauge (5 mbar) |
| Permitted Test Duration: | Calculated from pipe diameter and length (see Section 4) |
| Ambient Temperature: | °C |
| Weather Conditions: | e.g. Dry, overcast, 12°C |

# 4. Permitted Test Time Calculation

Per WIS 4-34-04: T = 0.077 × d × p (for pipes) + 0.15 per manhole, where T = time in seconds, d = nominal diameter in mm, p = number of pipe lengths. Minimum test time = 1 minute for any section.

| Pipe Diameter (d) mm: | mm |
| --- | --- |
| Number of Pipe Lengths (p): | Enter number |
| Number of Manholes: | Enter number included in test section |
| Calculated Test Time: | seconds (minimum 60 seconds) |
| Test Time Applied: | seconds |

# 5. Test Results

| Test No. | Section | Start Press. mm | End Press. mm | Time sec | Permitted sec | Result | Comments |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  | mm | mm | s | s | Pass/Fail |  |
| 2 |  | mm | mm | s | s | Pass/Fail |  |
| 3 |  | mm | mm | s | s | Pass/Fail |  |
| 4 |  | mm | mm | s | s | Pass/Fail |  |
| 5 |  | mm | mm | s | s | Pass/Fail |  |
| 6 |  | mm | mm | s | s | Pass/Fail |  |
| 7 |  | mm | mm | s | s | Pass/Fail |  |
| 8 |  | mm | mm | s | s | Pass/Fail |  |
| 9 |  | mm | mm | s | s | Pass/Fail |  |
| 10 |  | mm | mm | s | s | Pass/Fail |  |
| 11 |  | mm | mm | s | s | Pass/Fail |  |
| 12 |  | mm | mm | s | s | Pass/Fail |  |

# 6. Failed Test Actions

| Section(s) Failed: | List test numbers and sections that failed |
| --- | --- |
| Investigation / Repair: | Describe investigation and repair action taken |
| Re-Test Date: | DD / MM / YYYY |
| Re-Test Result: | Pass / Fail – enter re-test report reference |

# 7. Sign-Off

| Tested By |  | Witnessed By |  |
| --- | --- | --- | --- |
| Name: | Print name | Name: | Print name |
| Company: | Enter company | Position: | Enter role |
| Signature: |  | Signature: |  |
| Date: | DD / MM / YYYY | Date: | DD / MM / YYYY |

# 8. Document Control

| Revision | Date | Description of Change | Author | Approved By |
| --- | --- | --- | --- | --- |
| 01 | DD/MM/YYYY | Initial issue |  |  |
|  | DD/MM/YYYY |  |  |  |
|  | DD/MM/YYYY |  |  |  |