UV Disinfection System

Commissioning Record

| Document Ref: | Enter reference | Revision: | Enter revision |
| --- | --- | --- | --- |
| Project Name: | Enter project name | Contract No: | Enter contract number |
| Date: | DD / MM / YYYY | Commissioned By: | Name and company |
| Witnessed By: | Name and role | Approved By: | Name and role |

# 1. System Details

| UV System Tag / Ref: | Enter asset tag number |
| --- | --- |
| Manufacturer: | Enter manufacturer name |
| Model: | Enter model number |
| Serial Number: | Enter serial number |
| UV System Type: | e.g. Open channel, closed vessel (in-pipe), medium pressure, low pressure |
| Number of Banks / Modules: | Enter number |
| Lamps Per Bank: | Enter number of UV lamps per bank |
| Total Number of Lamps: | Enter total lamps installed |
| Lamp Type: | e.g. Low pressure high output (LPHO), medium pressure (MP), amalgam |
| Lamp Power (W per lamp): | W |
| Design UV Dose: | mJ/cm² (at end of lamp life, design UVT and flow) |
| Design Flow (DWF / FFT): | l/s or m³/hr |
| Design UVT (%T at 254nm): | % transmittance |
| Location: | Enter building or area on site |
| Drawing Reference: | Enter P&ID, GA, and wiring drawing references |

# 2. Pre-Commissioning Checks

| No. | Test / Check Item | Pass | Fail | N/A | Initials |
| --- | --- | --- | --- | --- | --- |
| 1 | UV system installed in accordance with manufacturer’s installation manual |  |  |  |  |
| 2 | Channel / vessel clean and free from construction debris |  |  |  |  |
| 3 | All lamps installed in correct positions and orientation |  |  |  |  |
| 4 | Quartz sleeves installed, clean, and free from cracks or damage |  |  |  |  |
| 5 | All O-rings and seals correctly fitted |  |  |  |  |
| 6 | UV intensity sensors (radiometers) installed and calibrated |  |  |  |  |
| 7 | Wiper / cleaning system installed and functional (mechanical or chemical) |  |  |  |  |
| 8 | Electrical supply connected and correct voltage confirmed |  |  |  |  |
| 9 | Control panel powered up – no fault alarms on start-up |  |  |  |  |
| 10 | Level control (weir gate or penstock) installed and set correctly |  |  |  |  |
| 11 | Inlet and outlet isolation gates / valves operational |  |  |  |  |
| 12 | UV safety interlocks tested (lamp compartment door, water level low) |  |  |  |  |
| 13 | UV warning signage displayed (do not look at UV light without protection) |  |  |  |  |
| 14 | UV-rated PPE available (face shield, UV-blocking glasses) |  |  |  |  |
| 15 | SCADA / BMS alarm connections wired and tested |  |  |  |  |

# 3. Lamp and Sensor Test Results

| Lamp No. | Bank / Module | Hours Run | Status | Output W | Intensity mW/cm² | Sensor Reading | Pass? |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  | hrs | ON / OFF | W | mW/cm² |  | Y / N |
| 2 |  | hrs | ON / OFF | W | mW/cm² |  | Y / N |
| 3 |  | hrs | ON / OFF | W | mW/cm² |  | Y / N |
| 4 |  | hrs | ON / OFF | W | mW/cm² |  | Y / N |
| 5 |  | hrs | ON / OFF | W | mW/cm² |  | Y / N |
| 6 |  | hrs | ON / OFF | W | mW/cm² |  | Y / N |
| 7 |  | hrs | ON / OFF | W | mW/cm² |  | Y / N |
| 8 |  | hrs | ON / OFF | W | mW/cm² |  | Y / N |
| 9 |  | hrs | ON / OFF | W | mW/cm² |  | Y / N |
| 10 |  | hrs | ON / OFF | W | mW/cm² |  | Y / N |
| 11 |  | hrs | ON / OFF | W | mW/cm² |  | Y / N |
| 12 |  | hrs | ON / OFF | W | mW/cm² |  | Y / N |

# 4. Functional Tests

| No. | Test / Check Item | Pass | Fail | N/A | Initials |
| --- | --- | --- | --- | --- | --- |
| 1 | All lamps ignite correctly on start-up (within specified warm-up time) |  |  |  |  |
| 2 | Lamp failure alarm tested (remove one lamp and verify alarm at SCADA) |  |  |  |  |
| 3 | Low UV intensity alarm tested (cover sensor and verify alarm) |  |  |  |  |
| 4 | High water level alarm tested and verified at SCADA |  |  |  |  |
| 5 | Low water level interlock tested (lamps off when water level drops) |  |  |  |  |
| 6 | Automatic wiper / cleaning cycle initiated and completed successfully |  |  |  |  |
| 7 | Manual wiper / cleaning cycle initiated from control panel |  |  |  |  |
| 8 | Lamp hour counter incrementing correctly |  |  |  |  |
| 9 | Lamp end-of-life alarm set correctly (state hours) |  |  |  |  |
| 10 | Duty / standby bank changeover tested (if applicable) |  |  |  |  |
| 11 | Dose pacing verified – lamps dim or switch off at low flows |  |  |  |  |
| 12 | Flow signal input verified from flow meter (4–20mA or digital) |  |  |  |  |
| 13 | UVT signal input verified from UVT analyser (if fitted) |  |  |  |  |
| 14 | All alarms, faults, and status points verified at SCADA |  |  |  |  |

# 5. Performance Test Results

| Parameter | Design Value | Measured Value | Pass / Fail |
| --- | --- | --- | --- |
| Flow rate during test (l/s) |  |  | P / F |
| UVT at 254nm (%T) |  |  | P / F |
| UV intensity at sensor (mW/cm²) |  |  | P / F |
| Calculated UV dose (mJ/cm²) |  |  | P / F |
| Number of lamps operating |  |  | P / F |
| Total power consumption (kW) |  |  | P / F |
| Water level in channel (mm) |  |  | P / F |
| Water temperature (°C) |  |  | P / F |
| Inlet TSS (mg/l) |  |  | P / F |
| Inlet E. coli (cfu/100ml) |  |  | P / F |
| Outlet E. coli (cfu/100ml) |  |  | P / F |
| Log reduction achieved |  |  | P / F |

# 6. Snags and Actions

| No. | Issue Description | Action Required | Owner | Status |
| --- | --- | --- | --- | --- |
| 1 |  |  |  | Open / Closed |
| 2 |  |  |  | Open / Closed |
| 3 |  |  |  | Open / Closed |
| 4 |  |  |  | Open / Closed |
| 5 |  |  |  | Open / Closed |
| 6 |  |  |  | Open / Closed |

# 7. Sign-Off

This record confirms that the UV disinfection system has been commissioned in accordance with the manufacturer’s procedures and project specification. All tests have been completed and results are within specified tolerances.

| Commissioning Engineer |  | Witness / Client Rep |  |
| --- | --- | --- | --- |
| Name: | Print name | Name: | Print name |
| Company: | Enter company | Position: | Enter role |
| Signature: |  | Signature: |  |
| Date: | DD / MM / YYYY | Date: | DD / MM / YYYY |

# 8. Document Control

| Revision | Date | Description of Change | Author | Approved By |
| --- | --- | --- | --- | --- |
| 01 | DD/MM/YYYY | Initial issue |  |  |
|  | DD/MM/YYYY |  |  |  |
|  | DD/MM/YYYY |  |  |  |