Centrifuge and Dewatering

Commissioning Record

| Document Ref: | Enter reference | Revision: | Enter revision |
| --- | --- | --- | --- |
| Project Name: | Enter project name | Contract No: | Enter contract number |
| Date: | DD / MM / YYYY | Commissioned By: | Name and company |
| Witnessed By: | Name and role | Approved By: | Name and role |

# 1. Equipment Details

| Centrifuge Tag / Ref: | Enter asset tag number |
| --- | --- |
| Manufacturer: | Enter manufacturer name |
| Model: | Enter model number |
| Serial Number: | Enter serial number |
| Type: | e.g. Decanter centrifuge, disc stack, belt press |
| Bowl Diameter (mm): | mm |
| Bowl Speed (RPM): | RPM (design maximum) |
| Main Drive Motor (kW): | kW |
| Scroll Drive / Back-Drive (kW): | kW |
| Design Throughput: | m³/hr of sludge |
| Design Feed DS (%): | % dry solids of feed sludge |
| Target Cake DS (%): | % dry solids of dewatered cake |
| Sludge Type: | e.g. Surplus activated sludge, primary, digested, thickened |
| Location: | Enter building and floor |
| Drawing Reference: | Enter P&ID and GA drawing references |

# 2. Pre-Commissioning Checks

| No. | Test / Check Item | Pass | Fail | N/A | Initials |
| --- | --- | --- | --- | --- | --- |
| 1 | Centrifuge installed level on vibration isolation mounts |  |  |  |  |
| 2 | All holding-down bolts torqued to manufacturer specification |  |  |  |  |
| 3 | Sludge feed pipework connected and flushed |  |  |  |  |
| 4 | Centrate return pipework connected and clear |  |  |  |  |
| 5 | Cake discharge chute / conveyor aligned and connected |  |  |  |  |
| 6 | Polymer dosing system connected and primed |  |  |  |  |
| 7 | Polymer make-up and aging tanks filled and tested |  |  |  |  |
| 8 | Wash water supply connected (adequate pressure and flow) |  |  |  |  |
| 9 | Bearing lubrication completed (grease or oil as specified) |  |  |  |  |
| 10 | Gearbox oil filled to correct level with specified grade |  |  |  |  |
| 11 | All guards and safety covers fitted and interlocked |  |  |  |  |
| 12 | VSD installed and configured for main drive and scroll drive |  |  |  |  |
| 13 | Odour extraction ducting connected to centrifuge housing |  |  |  |  |
| 14 | All electrical connections completed and insulation tested |  |  |  |  |
| 15 | SCADA / local control panel signals tested |  |  |  |  |

# 3. Commissioning Tests

| No. | Test / Check Item | Pass | Fail | N/A | Initials |
| --- | --- | --- | --- | --- | --- |
| 1 | Rotation direction verified for bowl and scroll (bump test) |  |  |  |  |
| 2 | Centrifuge run on clean water to check for leaks and vibration |  |  |  |  |
| 3 | Bowl speed increased incrementally to rated speed |  |  |  |  |
| 4 | Vibration measured and within manufacturer limits at rated speed |  |  |  |  |
| 5 | Bearing temperatures monitored and within limits during clean water run |  |  |  |  |
| 6 | Sludge feed introduced at low flow rate and gradually increased |  |  |  |  |
| 7 | Polymer dosing rate adjusted to achieve target cake dryness |  |  |  |  |
| 8 | Differential speed (bowl vs scroll) adjusted for optimal performance |  |  |  |  |
| 9 | Centrate quality assessed (clarity, TSS content) |  |  |  |  |
| 10 | Cake dry solids measured and compared to design target |  |  |  |  |
| 11 | Throughput tested at design capacity |  |  |  |  |
| 12 | Automatic start-up and shutdown sequence tested |  |  |  |  |
| 13 | Wash cycle tested (CIP) and duration verified |  |  |  |  |
| 14 | All alarms tested: high vibration, high torque, bearing temp, low flow |  |  |  |  |
| 15 | Emergency stop tested – controlled deceleration confirmed |  |  |  |  |
| 16 | Duty / standby changeover tested (if parallel installation) |  |  |  |  |

# 4. Performance Test Results

| Parameter | Design Value | Measured Value | Pass / Fail |
| --- | --- | --- | --- |
| Feed sludge flow rate (m³/hr) |  |  | P / F |
| Feed sludge DS (%) |  |  | P / F |
| Cake dry solids (%) |  |  | P / F |
| Centrate TSS (mg/l) |  |  | P / F |
| Solids capture rate (%) |  |  | P / F |
| Polymer dose (kg active / t DS) |  |  | P / F |
| Bowl speed (RPM) |  |  | P / F |
| Differential speed (RPM) |  |  | P / F |
| Main drive current (A) |  |  | P / F |
| Scroll drive torque (%) |  |  | P / F |
| Vibration – drive end (mm/s) |  |  | P / F |
| Vibration – non-drive end (mm/s) |  |  | P / F |
| Bearing temp – drive end (°C) |  |  | P / F |
| Bearing temp – non-drive end (°C) |  |  | P / F |
| Total power consumption (kW) |  |  | P / F |
| Noise at 1m (dBA) |  |  | P / F |

# 5. Snags and Actions

| No. | Issue | Action | Owner | Status |
| --- | --- | --- | --- | --- |
| 1 |  |  |  | Open / Closed |
| 2 |  |  |  | Open / Closed |
| 3 |  |  |  | Open / Closed |
| 4 |  |  |  | Open / Closed |
| 5 |  |  |  | Open / Closed |
| 6 |  |  |  | Open / Closed |

# 6. Sign-Off

| Commissioning Engineer |  | Witness / Client Rep |  |
| --- | --- | --- | --- |
| Name: | Print name | Name: | Print name |
| Company: | Enter company | Position: | Enter role |
| Signature: |  | Signature: |  |
| Date: | DD / MM / YYYY | Date: | DD / MM / YYYY |

# 7. Document Control

| Revision | Date | Description of Change | Author | Approved By |
| --- | --- | --- | --- | --- |
| 01 | DD/MM/YYYY | Initial issue |  |  |
|  | DD/MM/YYYY |  |  |  |
|  | DD/MM/YYYY |  |  |  |